## Clonee 220 kV
Terminal | Clonee 220 kV |  | Terminal | Clonee 220 kV
Terminal Name | Clonee 220 kV |  | Terminal Name | Clonee 220 kV_Corduff 110 kV |  | Clonee 220 kV_Corduff 220 kV |  | Clonee 220 kV_Cruiserath 220 kV |  | Clonee 220 kV_Woodland 220 kV
Study Case | step2 |  | Study Case | step2 |  | step2 |  | step2 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 7.8995 | 12.0373 | 50 | 2.7369 | 2.496 | 6.5243 | 5.5934 | 6.5244 | 5.5935 | 5.9809 | 6.6027
100 | 21.0684 | 28.548 | 100 | 8.0853 | 7.5501 | 18.5334 | 16.5878 | 18.5341 | 16.5884 | 17.3481 | 18.2595
150 | 26.1574 | 26.3041 | 150 | 13.3545 | 13.2255 | 27.12 | 27.2117 | 27.1224 | 27.2141 | 26.8142 | 25.2672
200 | 6.9963 | 21.5114 | 200 | 3.2543 | 3.7894 | 5.2835 | 6.6211 | 5.2843 | 6.6222 | 5.6127 | 4.3966
250 | 16.8858 | 34.3347 | 250 | 3.6081 | 3.0267 | 11.6803 | 7.4388 | 11.6832 | 7.4406 | 8.3231 | 9.4634
300 | 28.9217 | 38.5369 | 300 | 8.692 | 7.0431 | 28.5877 | 21.5943 | 28.5977 | 21.6019 | 20.4627 | 14.5594
350 | 11.6638 | 41.9199 | 350 | 6.6746 | 4.3237 | 18.563 | 12.7734 | 18.5719 | 12.7795 | 11.2438 | 5.8957
400 | 11.7802 | 55.481 | 400 | 1.969 | 1.9185 | 4.4364 | 2.1441 | 4.4392 | 2.1455 | 3.073 | 13.5243
450 | 22.8065 | 67.6612 | 450 | 5.2534 | 5.4588 | 9.4022 | 6.6091 | 9.4096 | 6.6143 | 10.5357 | 20.9127
500 | 37.363 | 76.265 | 500 | 17.9686 | 16.5799 | 29.5742 | 23.0994 | 29.603 | 23.1219 | 25.2945 | 28.5689
550 | 22.7737 | 82.5144 | 550 | 5.4522 | 9.4793 | 5.8732 | 3.9787 | 5.8801 | 3.9833 | 9.0887 | 25.4833
600 | 33.8099 | 90.872 | 600 | 7.1016 | 7.3391 | 16.2438 | 10.8381 | 16.2665 | 10.8532 | 16.396 | 29.0861
650 | 46.0436 | 110.2266 | 650 | 11.9643 | 10.0307 | 26.894 | 21.9561 | 26.9382 | 21.9921 | 28.3406 | 43.5293
700 | 55.4807 | 112.0775 | 700 | 30.0399 | 24.2952 | 39.0024 | 31.6892 | 39.0768 | 31.7496 | 36.7569 | 45.8021
750 | 56.4056 | 120.9132 | 750 | 57.9944 | 47.5026 | 40.7565 | 30.6148 | 40.8457 | 30.6818 | 35.6597 | 45.5876
800 | 72.57 | 149.3708 | 800 | 95.0668 | 88.2404 | 59.2848 | 52.9975 | 59.4324 | 53.1294 | 58.6423 | 73.9233
850 | 95.394 | 99.6146 | 850 | 65.1606 | 72.7546 | 109.3895 | 120.4272 | 109.6968 | 120.7656 | 114.7492 | 109.6686
900 | 23.3322 | 87.6915 | 900 | 29.8251 | 37.5861 | 41.9715 | 53.7425 | 42.1037 | 53.9118 | 44.8818 | 32.1481
950 | 10.8382 | 104.353 | 950 | 12.8469 | 20.2973 | 27.2567 | 40.5952 | 27.3524 | 40.7377 | 28.9667 | 12.9104
1000 | 15.3146 | 130.3251 | 1000 | 6.3084 | 10.1236 | 17.3885 | 30.4016 | 17.4562 | 30.5198 | 16.5215 | 26.5161
1050 | 24.8598 | 147.7483 | 1050 | 2.2062 | 5.6463 | 11.4377 | 16.1237 | 11.4868 | 16.1928 | 6.2188 | 40.1902
1100 | 35.5535 | 183.2387 | 1100 | 2.0362 | 4.3964 | 8.5286 | 10.0754 | 8.5687 | 10.1228 | 14.8554 | 70.1376
1150 | 51.7075 | 246.5955 | 1150 | 1.7115 | 5.8744 | 17.3474 | 31.072 | 17.4367 | 31.2319 | 46.5518 | 162.1512
1200 | 54.1189 | 142.7892 | 1200 | 0.24104 | 2.2194 | 37.3069 | 50.1927 | 37.5161 | 50.4742 | 70.4924 | 113.107
1250 | 19.1566 | 99.2709 | 1250 | 0.18594 | 1.1388 | 30.675 | 54.8432 | 30.8617 | 55.177 | 54.9522 | 66.9535
1300 | 21.9779 | 124.4252 | 1300 | 0.94742 | 0.66156 | 17.471 | 40.9476 | 17.5861 | 41.2172 | 37.5682 | 55.1954
1350 | 21.7276 | 108.5616 | 1350 | 2.0222 | 3.8443 | 15.4899 | 38.9175 | 15.6 | 39.194 | 42.127 | 58.2633
1400 | 25.2581 | 120.7781 | 1400 | 3.8737 | 9.7844 | 11.8354 | 37.5513 | 11.9259 | 37.8383 | 35.6375 | 37.686
1450 | 30.4703 | 135.8237 | 1450 | 3.6237 | 17.2497 | 7.443 | 36.2925 | 7.5041 | 36.5902 | 30.6631 | 26.2649
1500 | 35.4013 | 151.666 | 1500 | 2.7445 | 8.7829 | 6.3516 | 36.6835 | 6.4074 | 37.0056 | 27.2461 | 15.5486
1550 | 38.7793 | 167.3479 | 1550 | 2.1495 | 5.4982 | 3.8304 | 40.2389 | 3.8663 | 40.6165 | 25.6274 | 7.2666
1600 | 41.4256 | 182.4254 | 1600 | 5.2117 | 11.7699 | 4.2098 | 44.435 | 4.2519 | 44.8795 | 24.8787 | 7.2627
1650 | 43.9114 | 200.0234 | 1650 | 1.4125 | 8.2183 | 5.8013 | 49.6279 | 5.863 | 50.1562 | 23.999 | 16.3654
1700 | 49.9443 | 218.6676 | 1700 | 0.59155 | 7.9471 | 11.7127 | 62.8225 | 11.8451 | 63.5328 | 24.7007 | 34.7357
1750 | 45.946 | 219.1972 | 1750 | 0.44847 | 5.7435 | 8.1853 | 40.8733 | 8.2835 | 41.3633 | 18.1707 | 30.3553
1800 | 51.6084 | 221.2011 | 1800 | 0.43112 | 6.2037 | 5.9257 | 46.0852 | 6.0009 | 46.6701 | 20.5765 | 29.4309
1850 | 53.5342 | 233.2672 | 1850 | 2.1838 | 8.2335 | 8.0996 | 46.3962 | 8.2082 | 47.0187 | 19.6892 | 28.2502
1900 | 57.7826 | 261.8158 | 1900 | 1.615 | 8.3345 | 8.885 | 65.75 | 9.0108 | 66.6811 | 21.9725 | 45.9939
1950 | 63.9588 | 286.9115 | 1950 | 2.3027 | 10.5819 | 17.7 | 99.0759 | 17.9642 | 100.5548 | 26.3145 | 77.8259
2000 | 57.7616 | 246.0338 | 2000 | 2.0423 | 3.3593 | 16.9923 | 42.0403 | 17.2594 | 42.7009 | 17.3004 | 36.2816

## Corduff 110 kV
Terminal | Corduff 110 kV |  | Terminal | Corduff 110 kV
Terminal Name | Corduff 110 kV |  | Terminal Name | Corduff 110 kV_Clonee 220 kV |  | Corduff 110 kV_Corduff 220 kV |  | Corduff 110 kV_Cruiserath 220 kV |  | Corduff 110 kV_Woodland 220 kV
Study Case | step2 |  | Study Case | step2 |  | step2 |  | step2 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 3.4854 | 3.4994 | 50 | 2.7369 | 2.496 | 2.8183 | 2.8719 | 2.8183 | 2.8719 | 2.5462 | 2.5098
100 | 8.0092 | 8.0493 | 100 | 8.0853 | 7.5501 | 8.2717 | 8.4089 | 8.272 | 8.4092 | 7.7007 | 7.6303
150 | 6.7873 | 6.8464 | 150 | 13.3545 | 13.2255 | 13.4278 | 13.5476 | 13.429 | 13.5488 | 13.3653 | 13.4056
200 | 7.8605 | 7.9042 | 200 | 3.2543 | 3.7894 | 3.1116 | 3.0476 | 3.1121 | 3.0481 | 3.7158 | 3.8259
250 | 12.2097 | 12.3015 | 250 | 3.6081 | 3.0267 | 3.923 | 4.2878 | 3.924 | 4.2889 | 3.1156 | 3.1142
300 | 14.9524 | 14.8265 | 300 | 8.692 | 7.0431 | 9.4346 | 10.5342 | 9.4379 | 10.5379 | 7.2427 | 7.3261
350 | 17.3635 | 17.3372 | 350 | 6.6746 | 4.3237 | 7.3611 | 7.2888 | 7.3646 | 7.2923 | 5.1849 | 4.5056
400 | 23.4843 | 23.5236 | 400 | 1.969 | 1.9185 | 2.155 | 2.0873 | 2.1563 | 2.0886 | 1.8955 | 1.9591
450 | 32.3664 | 32.3538 | 450 | 5.2534 | 5.4588 | 5.2202 | 5.223 | 5.2243 | 5.2271 | 5.5259 | 5.5774
500 | 38.2201 | 38.2708 | 500 | 17.9686 | 16.5799 | 18.4208 | 18.6919 | 18.4388 | 18.7101 | 17.2697 | 17.0157
550 | 48.8539 | 48.524 | 550 | 5.4522 | 9.4793 | 4.4461 | 4.3342 | 4.4514 | 4.3393 | 8.4267 | 9.5339
600 | 49.9628 | 50.7902 | 600 | 7.1016 | 7.3391 | 8.2931 | 8.715 | 8.3047 | 8.7272 | 6.9959 | 7.3737
650 | 56.9114 | 57.3711 | 650 | 11.9643 | 10.0307 | 12.8501 | 13.0149 | 12.8713 | 13.0363 | 10.643 | 10.1928
700 | 94.3203 | 95.6378 | 700 | 30.0399 | 24.2952 | 32.0458 | 32.9808 | 32.1068 | 33.0436 | 26.0998 | 24.8381
750 | 127.9566 | 129.3579 | 750 | 57.9944 | 47.5026 | 61.4978 | 63.3577 | 61.6323 | 63.4963 | 50.2877 | 48.2587
800 | 63.4206 | 64.475 | 800 | 95.0668 | 88.2404 | 96.7435 | 96.8548 | 96.9843 | 97.0959 | 91.708 | 89.5096
850 | 92.7857 | 91.8467 | 850 | 65.1606 | 72.7546 | 63.0329 | 63.0795 | 63.21 | 63.2567 | 71.0072 | 73.5905
900 | 92.3073 | 92.1694 | 900 | 29.8251 | 37.5861 | 27.5914 | 26.8242 | 27.6783 | 26.9087 | 35.5497 | 37.8791
950 | 76.5055 | 75.9092 | 950 | 12.8469 | 20.2973 | 10.8399 | 10.0342 | 10.878 | 10.0694 | 18.2306 | 20.4745
1000 | 49.4158 | 49.3233 | 1000 | 6.3084 | 10.1236 | 5.3019 | 4.8552 | 5.3226 | 4.8741 | 8.8843 | 10.1748
1050 | 33.2279 | 33.1621 | 1050 | 2.2062 | 5.6463 | 1.2742 | 1.0997 | 1.2796 | 1.1044 | 4.5903 | 5.6642
1100 | 27.1945 | 27.1341 | 1100 | 2.0362 | 4.3964 | 1.678 | 1.6578 | 1.6859 | 1.6656 | 3.4337 | 4.2957
1150 | 19.3753 | 19.4068 | 1150 | 1.7115 | 5.8744 | 0.80399 | 0.56542 | 0.80813 | 0.56833 | 3.9999 | 5.8066
1200 | 13.7475 | 13.6934 | 1200 | 0.24104 | 2.2194 | 0.98639 | 1.5613 | 0.99192 | 1.57 | 1.9673 | 2.1848
1250 | 7.2516 | 7.2369 | 1250 | 0.18594 | 1.1388 | 0.41443 | 0.72392 | 0.41696 | 0.72833 | 1.0998 | 1.1141
1300 | 4.9577 | 4.9577 | 1300 | 0.94742 | 0.66156 | 1.0672 | 1.1623 | 1.0742 | 1.17 | 0.60458 | 0.6468
1350 | 17.5891 | 17.6367 | 1350 | 2.0222 | 3.8443 | 1.3151 | 0.9506 | 1.3245 | 0.95736 | 3.8653 | 3.7203
1400 | 49.8274 | 50.2026 | 1400 | 3.8737 | 9.7844 | 2.1977 | 2.3406 | 2.2145 | 2.3585 | 9.3941 | 9.4323
1450 | 98.5652 | 97.8306 | 1450 | 3.6237 | 17.2497 | 2.9273 | 6.5731 | 2.9513 | 6.627 | 15.6541 | 16.509
1500 | 56.1781 | 55.5769 | 1500 | 2.7445 | 8.7829 | 3.903 | 6.0176 | 3.9373 | 6.0705 | 7.5485 | 8.3409
1550 | 34.8275 | 34.6579 | 1550 | 2.1495 | 5.4982 | 2.4527 | 3.5618 | 2.4757 | 3.5953 | 4.8675 | 5.5168
1600 | 75.7653 | 75.2913 | 1600 | 5.2117 | 11.7699 | 4.254 | 4.9937 | 4.2965 | 5.0437 | 10.1892 | 11.6322
1650 | 46.3339 | 46.1249 | 1650 | 1.4125 | 8.2183 | 1.2338 | 3.0279 | 1.2469 | 3.0601 | 6.1521 | 7.8985
1700 | 31.3386 | 30.9358 | 1700 | 0.59155 | 7.9471 | 2.7319 | 6.1049 | 2.7628 | 6.1739 | 5.0112 | 7.484
1750 | 29.249 | 29.0542 | 1750 | 0.44847 | 5.7435 | 1.5155 | 2.8035 | 1.5336 | 2.8371 | 4.0621 | 5.2242
1800 | 37.7429 | 37.5161 | 1800 | 0.43112 | 6.2037 | 2.054 | 3.9003 | 2.08 | 3.9498 | 4.4171 | 5.6966
1850 | 32.414 | 31.8459 | 1850 | 2.1838 | 8.2335 | 5.0015 | 7.5226 | 5.0686 | 7.6235 | 5.2396 | 7.5069
1900 | 32.5296 | 32.1659 | 1900 | 1.615 | 8.3345 | 3.9466 | 7.4015 | 4.0025 | 7.5063 | 4.6864 | 7.5179
1950 | 25.7142 | 25.4681 | 1950 | 2.3027 | 10.5819 | 5.0271 | 10.7078 | 5.1021 | 10.8677 | 4.9506 | 9.4757
2000 | 21.0366 | 21.1787 | 2000 | 2.0423 | 3.3593 | 3.6049 | 4.36 | 3.6615 | 4.4285 | 2.529 | 2.9849

## Corduff 220 kV
Terminal | Corduff 220 kV |  | Terminal | Corduff 220 kV
Terminal Name | Corduff 220 kV |  | Terminal Name | Corduff 220 kV_Clonee 220 kV |  | Corduff 220 kV_Corduff 110 kV |  | Corduff 220 kV_Cruiserath 220 kV |  | Corduff 220 kV_Woodland 220 kV
Study Case | step2 |  | Study Case | step2 |  | step2 |  | step2 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 6.838 | 7.0452 | 50 | 6.5243 | 5.5934 | 2.8183 | 2.8719 | 6.8381 | 7.0453 | 5.7758 | 5.6356
100 | 19.2123 | 19.7207 | 100 | 18.5334 | 16.5878 | 8.2717 | 8.4089 | 19.213 | 19.7215 | 17.0379 | 16.7866
150 | 27.2316 | 27.5759 | 150 | 27.12 | 27.2117 | 13.4278 | 13.5476 | 27.234 | 27.5784 | 27.3252 | 27.5682
200 | 5.4232 | 5.8017 | 200 | 5.2835 | 6.6211 | 3.1116 | 3.0476 | 5.424 | 5.8026 | 6.2216 | 6.6427
250 | 13.4544 | 15.2052 | 250 | 11.6803 | 7.4388 | 3.923 | 4.2878 | 13.4577 | 15.2089 | 8.0765 | 7.7603
300 | 31.6624 | 35.8586 | 300 | 28.5877 | 21.5943 | 9.4346 | 10.5342 | 31.6735 | 35.8712 | 22.2854 | 22.4815
350 | 20.4212 | 20.5204 | 350 | 18.563 | 12.7734 | 7.3611 | 7.2888 | 20.431 | 20.5302 | 14.7057 | 13.2616
400 | 5.1449 | 5.1041 | 400 | 4.4364 | 2.1441 | 2.155 | 2.0873 | 5.1481 | 5.1073 | 2.8154 | 2.2285
450 | 10.2539 | 10.4334 | 450 | 9.4022 | 6.6091 | 5.2202 | 5.223 | 10.262 | 10.4416 | 7.4754 | 6.8112
500 | 31.7499 | 32.9498 | 500 | 29.5742 | 23.0994 | 18.4208 | 18.6919 | 31.7808 | 32.9819 | 24.9499 | 23.7707
550 | 6.4321 | 6.505 | 550 | 5.8732 | 3.9787 | 4.4461 | 4.3342 | 6.4396 | 6.5126 | 4.6016 | 4.0653
600 | 17.9214 | 18.4232 | 600 | 16.2438 | 10.8381 | 8.2931 | 8.715 | 17.9465 | 18.449 | 12.4652 | 11.183
650 | 28.3268 | 28.5787 | 650 | 26.894 | 21.9561 | 12.8501 | 13.0149 | 28.3733 | 28.6256 | 23.7302 | 22.4123
700 | 41.52 | 42.6804 | 700 | 39.0024 | 31.6892 | 32.0458 | 32.9808 | 41.5991 | 42.7617 | 33.9529 | 32.3401
750 | 43.8682 | 45.1671 | 750 | 40.7565 | 30.6148 | 61.4978 | 63.3577 | 43.9641 | 45.2659 | 33.4067 | 31.1621
800 | 60.8137 | 60.6593 | 800 | 59.2848 | 52.9975 | 96.7435 | 96.8548 | 60.965 | 60.8102 | 55.8494 | 53.7737
850 | 106.3311 | 106.6969 | 850 | 109.3895 | 120.4272 | 63.0329 | 63.0795 | 106.6298 | 106.9966 | 117.7517 | 121.7615
900 | 38.5989 | 37.3766 | 900 | 41.9715 | 53.7425 | 27.5914 | 26.8242 | 38.7205 | 37.4943 | 50.6639 | 54.1123
950 | 23.8084 | 22.6005 | 950 | 27.2567 | 40.5952 | 10.8399 | 10.0342 | 23.892 | 22.6798 | 36.6213 | 40.6823
1000 | 14.3212 | 13.5903 | 1000 | 17.3885 | 30.4016 | 5.3019 | 4.8552 | 14.3769 | 13.6431 | 25.9511 | 30.2227
1050 | 11.3924 | 12.3834 | 1050 | 11.4377 | 16.1237 | 1.2742 | 1.0997 | 11.4413 | 12.4365 | 14.7128 | 16.0384
1100 | 8.2695 | 8.2609 | 1100 | 8.5286 | 10.0754 | 1.678 | 1.6578 | 8.3084 | 8.2998 | 9.6901 | 10.1314
1150 | 14.0421 | 12.3239 | 1150 | 17.3474 | 31.072 | 0.80399 | 0.56542 | 14.1144 | 12.3874 | 26.1226 | 30.8216
1200 | 31.0999 | 25.4323 | 1200 | 37.3069 | 50.1927 | 0.98639 | 1.5613 | 31.2743 | 25.5749 | 55.3763 | 49.4792
1250 | 21.6654 | 14.6809 | 1250 | 30.675 | 54.8432 | 0.41443 | 0.72392 | 21.7972 | 14.7703 | 53.2789 | 53.7509
1300 | 9.8097 | 6.8559 | 1300 | 17.471 | 40.9476 | 1.0672 | 1.1623 | 9.8743 | 6.901 | 38.1854 | 39.9144
1350 | 6.8926 | 5.8088 | 1350 | 15.4899 | 38.9175 | 1.3151 | 0.9506 | 6.9416 | 5.8501 | 39.0469 | 37.7015
1400 | 4.656 | 8.3727 | 1400 | 11.8354 | 37.5513 | 2.1977 | 2.3406 | 4.6915 | 8.4367 | 35.7906 | 36.1705
1450 | 4.6996 | 12.5194 | 1450 | 7.443 | 36.2925 | 2.9273 | 6.5731 | 4.7381 | 12.6221 | 32.8916 | 34.7634
1500 | 9.3465 | 18.2728 | 1500 | 6.3516 | 36.6835 | 3.903 | 6.0176 | 9.4286 | 18.4333 | 31.4023 | 34.9476
1550 | 11.3065 | 22.9176 | 1550 | 3.8304 | 40.2389 | 2.4527 | 3.5618 | 11.4126 | 23.1326 | 31.982 | 38.1018
1600 | 13.6645 | 27.5235 | 1600 | 4.2098 | 44.435 | 4.254 | 4.9937 | 13.8011 | 27.7989 | 33.0853 | 41.7101
1650 | 16.576 | 33.3127 | 1650 | 5.8013 | 49.6279 | 1.2338 | 3.0279 | 16.7525 | 33.6673 | 34.5083 | 46.3448
1700 | 28.9206 | 58.8852 | 1700 | 11.7127 | 62.8225 | 2.7319 | 6.1049 | 29.2476 | 59.5509 | 38.7923 | 58.2639
1750 | 14.4833 | 24.4689 | 1750 | 8.1853 | 40.8733 | 1.5155 | 2.8035 | 14.6569 | 24.7623 | 30.302 | 37.7999
1800 | 19.3083 | 33.8909 | 1800 | 5.9257 | 46.0852 | 2.054 | 3.9003 | 19.5534 | 34.3211 | 32.2981 | 42.2131
1850 | 20.956 | 35.5938 | 1850 | 8.0996 | 46.3962 | 5.0015 | 7.5226 | 21.2372 | 36.0714 | 31.8705 | 42.1556
1900 | 26.5516 | 52.4435 | 1900 | 8.885 | 65.75 | 3.9466 | 7.4015 | 26.9276 | 53.1861 | 37.7354 | 59.2282
1950 | 42.4292 | 94.5501 | 1950 | 17.7 | 99.0759 | 5.0271 | 10.7078 | 43.0625 | 95.9614 | 47.631 | 88.5098
2000 | 32.8203 | 42.7291 | 2000 | 16.9923 | 42.0403 | 3.6049 | 4.36 | 33.336 | 43.4005 | 32.9138 | 37.2221

## Cruiserath 220 kV
Terminal | Cruiserath 220 kV |  | Terminal | Cruiserath 220 kV
Terminal Name | Cruiserath 220 kV |  | Terminal Name | Cruiserath 220 kV_Clonee 220 kV |  | Cruiserath 220 kV_Corduff 110 kV |  | Cruiserath 220 kV_Corduff 220 kV |  | Cruiserath 220 kV_Woodland 220 kV
Study Case | step2 |  | Study Case | step2 |  | step2 |  | step2 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 6.9407 | 7.148 | 50 | 6.5244 | 5.5935 | 2.8183 | 2.8719 | 6.8381 | 7.0453 | 5.7758 | 5.6356
100 | 19.4076 | 19.9167 | 100 | 18.5341 | 16.5884 | 8.272 | 8.4092 | 19.213 | 19.7215 | 17.0386 | 16.7872
150 | 27.1715 | 27.5234 | 150 | 27.1224 | 27.2141 | 13.429 | 13.5488 | 27.234 | 27.5784 | 27.3276 | 27.5706
200 | 5.4818 | 5.9185 | 200 | 5.2843 | 6.6222 | 3.1121 | 3.0481 | 5.424 | 5.8026 | 6.2225 | 6.6438
250 | 13.8645 | 15.6246 | 250 | 11.6832 | 7.4406 | 3.924 | 4.2889 | 13.4577 | 15.2089 | 8.0785 | 7.7622
300 | 31.8325 | 35.9972 | 300 | 28.5977 | 21.6019 | 9.4379 | 10.5379 | 31.6735 | 35.8712 | 22.2933 | 22.4894
350 | 19.9715 | 20.0405 | 350 | 18.5719 | 12.7795 | 7.3646 | 7.2923 | 20.431 | 20.5302 | 14.7127 | 13.268
400 | 4.8425 | 4.7856 | 400 | 4.4392 | 2.1455 | 2.1563 | 2.0886 | 5.1481 | 5.1073 | 2.8172 | 2.2299
450 | 11.1147 | 11.2953 | 450 | 9.4096 | 6.6143 | 5.2243 | 5.2271 | 10.262 | 10.4416 | 7.4813 | 6.8166
500 | 32.2852 | 33.4816 | 500 | 29.603 | 23.1219 | 18.4388 | 18.7101 | 31.7808 | 32.9819 | 24.9742 | 23.7938
550 | 7.4471 | 7.5227 | 550 | 5.8801 | 3.9833 | 4.4514 | 4.3393 | 6.4396 | 6.5126 | 4.607 | 4.0701
600 | 19.1398 | 19.6472 | 600 | 16.2665 | 10.8532 | 8.3047 | 8.7272 | 17.9465 | 18.449 | 12.4827 | 11.1987
650 | 29.6639 | 29.9212 | 650 | 26.9382 | 21.9921 | 12.8713 | 13.0363 | 28.3733 | 28.6256 | 23.7692 | 22.4492
700 | 42.8027 | 43.9997 | 700 | 39.0768 | 31.7496 | 32.1068 | 33.0436 | 41.5991 | 42.7617 | 34.0176 | 32.4018
750 | 45.0462 | 46.346 | 750 | 40.8457 | 30.6818 | 61.6323 | 63.4963 | 43.9641 | 45.2659 | 33.4797 | 31.2302
800 | 61.7625 | 61.6169 | 800 | 59.4324 | 53.1294 | 96.9843 | 97.0959 | 60.965 | 60.8102 | 55.9884 | 53.9075
850 | 105.7922 | 106.1904 | 850 | 109.6968 | 120.7656 | 63.21 | 63.2567 | 106.6298 | 106.9966 | 118.0825 | 122.1036
900 | 37.2859 | 36.0698 | 900 | 42.1037 | 53.9118 | 27.6783 | 26.9087 | 38.7205 | 37.4943 | 50.8235 | 54.2828
950 | 22.3106 | 21.1792 | 950 | 27.3524 | 40.7377 | 10.878 | 10.0694 | 23.892 | 22.6798 | 36.7499 | 40.8251
1000 | 12.7178 | 12.1401 | 1000 | 17.4562 | 30.5198 | 5.3226 | 4.8741 | 14.3769 | 13.6431 | 26.052 | 30.3403
1050 | 10.3412 | 11.4103 | 1050 | 11.4868 | 16.1928 | 1.2796 | 1.1044 | 11.4413 | 12.4365 | 14.7759 | 16.1072
1100 | 8.3529 | 8.3846 | 1100 | 8.5687 | 10.1228 | 1.6859 | 1.6656 | 8.3084 | 8.2998 | 9.7358 | 10.1791
1150 | 15.4574 | 13.6552 | 1150 | 17.4367 | 31.2319 | 0.80813 | 0.56833 | 14.1144 | 12.3874 | 26.2571 | 30.9803
1200 | 31.7509 | 26.3053 | 1200 | 37.5161 | 50.4742 | 0.99192 | 1.57 | 31.2743 | 25.5749 | 55.6867 | 49.7566
1250 | 19.9452 | 13.2138 | 1250 | 30.8617 | 55.177 | 0.41696 | 0.72833 | 21.7972 | 14.7703 | 53.6032 | 54.078
1300 | 8.2854 | 7.219 | 1300 | 17.5861 | 41.2172 | 1.0742 | 1.17 | 9.8743 | 6.901 | 38.4368 | 40.1772
1350 | 5.6277 | 7.5591 | 1350 | 15.6 | 39.194 | 1.3245 | 0.95736 | 6.9416 | 5.8501 | 39.3243 | 37.9693
1400 | 4.9789 | 10.8443 | 1400 | 11.9259 | 37.8383 | 2.2145 | 2.3585 | 4.6915 | 8.4367 | 36.0642 | 36.447
1450 | 7.2133 | 15.4889 | 1450 | 7.5041 | 36.5902 | 2.9513 | 6.627 | 4.7381 | 12.6221 | 33.1614 | 35.0486
1500 | 11.9734 | 21.3332 | 1500 | 6.4074 | 37.0056 | 3.9373 | 6.0705 | 9.4286 | 18.4333 | 31.6781 | 35.2545
1550 | 14.4374 | 26.3342 | 1550 | 3.8663 | 40.6165 | 2.4757 | 3.5953 | 11.4126 | 23.1326 | 32.2821 | 38.4593
1600 | 16.9238 | 31.1124 | 1600 | 4.2519 | 44.8795 | 4.2965 | 5.0437 | 13.8011 | 27.7989 | 33.4163 | 42.1273
1650 | 19.8283 | 36.8986 | 1650 | 5.863 | 50.1562 | 1.2469 | 3.0601 | 16.7525 | 33.6673 | 34.8756 | 46.8381
1700 | 32.413 | 62.502 | 1700 | 11.8451 | 63.5328 | 2.7628 | 6.1739 | 29.2476 | 59.5509 | 39.2309 | 58.9226
1750 | 16.7367 | 26.6913 | 1750 | 8.2835 | 41.3633 | 1.5336 | 2.8371 | 14.6569 | 24.7623 | 30.6653 | 38.253
1800 | 22.9647 | 37.5368 | 1800 | 6.0009 | 46.6701 | 2.08 | 3.9498 | 19.5534 | 34.3211 | 32.708 | 42.7488
1850 | 24.4959 | 39.1188 | 1850 | 8.2082 | 47.0187 | 5.0686 | 7.6235 | 21.2372 | 36.0714 | 32.298 | 42.7211
1900 | 30.9309 | 57.2592 | 1900 | 9.0108 | 66.6811 | 4.0025 | 7.5063 | 26.9276 | 53.1861 | 38.2697 | 60.0669
1950 | 47.2602 | 99.8402 | 1950 | 17.9642 | 100.5548 | 5.1021 | 10.8677 | 43.0625 | 95.9614 | 48.3419 | 89.8309
2000 | 34.9648 | 43.6218 | 2000 | 17.2594 | 42.7009 | 3.6615 | 4.4285 | 33.336 | 43.4005 | 33.4309 | 37.807

## Woodland 220 kV
Terminal | Woodland 220 kV |  | Terminal | Woodland 220 kV
Terminal Name | Woodland 220 kV |  | Terminal Name | Woodland 220 kV_Clonee 220 kV |  | Woodland 220 kV_Corduff 110 kV |  | Woodland 220 kV_Corduff 220 kV |  | Woodland 220 kV_Cruiserath 220 kV
Study Case | step2 |  | Study Case | step2 |  | step2 |  | step2 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 6.5671 | 6.6602 | 50 | 5.9809 | 6.6027 | 2.5462 | 2.5098 | 5.7758 | 5.6356 | 5.7758 | 5.6356
100 | 18.3877 | 18.4959 | 100 | 17.3481 | 18.2595 | 7.7007 | 7.6303 | 17.0379 | 16.7866 | 17.0386 | 16.7872
150 | 25.9291 | 25.5947 | 150 | 26.8142 | 25.2672 | 13.3653 | 13.4056 | 27.3252 | 27.5682 | 27.3276 | 27.5706
200 | 4.6136 | 4.4672 | 200 | 5.6127 | 4.3966 | 3.7158 | 3.8259 | 6.2216 | 6.6427 | 6.2225 | 6.6438
250 | 9.8013 | 9.9124 | 250 | 8.3231 | 9.4634 | 3.1156 | 3.1142 | 8.0765 | 7.7603 | 8.0785 | 7.7622
300 | 17.1497 | 15.1638 | 300 | 20.4627 | 14.5594 | 7.2427 | 7.3261 | 22.2854 | 22.4815 | 22.2933 | 22.4894
350 | 5.622 | 6.0774 | 350 | 11.2438 | 5.8957 | 5.1849 | 4.5056 | 14.7057 | 13.2616 | 14.7127 | 13.268
400 | 11.0738 | 13.9339 | 400 | 3.073 | 13.5243 | 1.8955 | 1.9591 | 2.8154 | 2.2285 | 2.8172 | 2.2299
450 | 19.0803 | 21.5573 | 450 | 10.5357 | 20.9127 | 5.5259 | 5.5774 | 7.4754 | 6.8112 | 7.4813 | 6.8166
500 | 28.7958 | 29.3905 | 500 | 25.2945 | 28.5689 | 17.2697 | 17.0157 | 24.9499 | 23.7707 | 24.9742 | 23.7938
550 | 21.5469 | 26.1112 | 550 | 9.0887 | 25.4833 | 8.4267 | 9.5339 | 4.6016 | 4.0653 | 4.607 | 4.0701
600 | 27.0646 | 29.8793 | 600 | 16.396 | 29.0861 | 6.9959 | 7.3737 | 12.4652 | 11.183 | 12.4827 | 11.1987
650 | 40.8686 | 44.4909 | 650 | 28.3406 | 43.5293 | 10.643 | 10.1928 | 23.7302 | 22.4123 | 23.7692 | 22.4492
700 | 45.0517 | 46.7725 | 700 | 36.7569 | 45.8021 | 26.0998 | 24.8381 | 33.9529 | 32.3401 | 34.0176 | 32.4018
750 | 44.2602 | 46.4418 | 750 | 35.6597 | 45.5876 | 50.2877 | 48.2587 | 33.4067 | 31.1621 | 33.4797 | 31.2302
800 | 70.0072 | 75.0062 | 800 | 58.6423 | 73.9233 | 91.708 | 89.5096 | 55.8494 | 53.7737 | 55.9884 | 53.9075
850 | 108.7584 | 110.88 | 850 | 114.7492 | 109.6686 | 71.0072 | 73.5905 | 117.7517 | 121.7615 | 118.0825 | 122.1036
900 | 33.0108 | 32.3317 | 900 | 44.8818 | 32.1481 | 35.5497 | 37.8791 | 50.6639 | 54.1123 | 50.8235 | 54.2828
950 | 12.7344 | 12.9727 | 950 | 28.9667 | 12.9104 | 18.2306 | 20.4745 | 36.6213 | 40.6823 | 36.7499 | 40.8251
1000 | 13.8967 | 26.4754 | 1000 | 16.5215 | 26.5161 | 8.8843 | 10.1748 | 25.9511 | 30.2227 | 26.052 | 30.3403
1050 | 26.5327 | 40.0404 | 1050 | 6.2188 | 40.1902 | 4.5903 | 5.6642 | 14.7128 | 16.0384 | 14.7759 | 16.1072
1100 | 48.1985 | 69.9531 | 1100 | 14.8554 | 70.1376 | 3.4337 | 4.2957 | 9.6901 | 10.1314 | 9.7358 | 10.1791
1150 | 104.733 | 160.8057 | 1150 | 46.5518 | 162.1512 | 3.9999 | 5.8066 | 26.1226 | 30.8216 | 26.2571 | 30.9803
1200 | 107.951 | 111.4819 | 1200 | 70.4924 | 113.107 | 1.9673 | 2.1848 | 55.3763 | 49.4792 | 55.6867 | 49.7566
1250 | 60.6041 | 65.6119 | 1250 | 54.9522 | 66.9535 | 1.0998 | 1.1141 | 53.2789 | 53.7509 | 53.6032 | 54.078
1300 | 45.2411 | 53.7908 | 1300 | 37.5682 | 55.1954 | 0.60458 | 0.6468 | 38.1854 | 39.9144 | 38.4368 | 40.1772
1350 | 52.8627 | 56.4434 | 1350 | 42.127 | 58.2633 | 3.8653 | 3.7203 | 39.0469 | 37.7015 | 39.3243 | 37.9693
1400 | 34.7079 | 36.2874 | 1400 | 35.6375 | 37.686 | 9.3941 | 9.4323 | 35.7906 | 36.1705 | 36.0642 | 36.447
1450 | 24.2364 | 25.1444 | 1450 | 30.6631 | 26.2649 | 15.6541 | 16.509 | 32.8916 | 34.7634 | 33.1614 | 35.0486
1500 | 15.2891 | 14.7999 | 1500 | 27.2461 | 15.5486 | 7.5485 | 8.3409 | 31.4023 | 34.9476 | 31.6781 | 35.2545
1550 | 8.2803 | 6.9236 | 1550 | 25.6274 | 7.2666 | 4.8675 | 5.5168 | 31.982 | 38.1018 | 32.2821 | 38.4593
1600 | 4.3431 | 6.8263 | 1600 | 24.8787 | 7.2627 | 10.1892 | 11.6322 | 33.0853 | 41.7101 | 33.4163 | 42.1273
1650 | 5.9816 | 15.2071 | 1650 | 23.999 | 16.3654 | 6.1521 | 7.8985 | 34.5083 | 46.3448 | 34.8756 | 46.8381
1700 | 14.4986 | 32.1439 | 1700 | 24.7007 | 34.7357 | 5.0112 | 7.484 | 38.7923 | 58.2639 | 39.2309 | 58.9226
1750 | 17.206 | 28.1018 | 1750 | 18.1707 | 30.3553 | 4.0621 | 5.2242 | 30.302 | 37.7999 | 30.6653 | 38.253
1800 | 16.0432 | 26.972 | 1800 | 20.5765 | 29.4309 | 4.4171 | 5.6966 | 32.2981 | 42.2131 | 32.708 | 42.7488
1850 | 15.0279 | 25.6635 | 1850 | 19.6892 | 28.2502 | 5.2396 | 7.5069 | 31.8705 | 42.1556 | 32.298 | 42.7211
1900 | 21.2664 | 41.4286 | 1900 | 21.9725 | 45.9939 | 4.6864 | 7.5179 | 37.7354 | 59.2282 | 38.2697 | 60.0669
1950 | 31.3363 | 69.5266 | 1950 | 26.3145 | 77.8259 | 4.9506 | 9.4757 | 47.631 | 88.5098 | 48.3419 | 89.8309
2000 | 24.547 | 32.1202 | 2000 | 17.3004 | 36.2816 | 2.529 | 2.9849 | 32.9138 | 37.2221 | 33.4309 | 37.807