## Cover Sheet
PSC Harmonics Input Spreadsheet
Reference Document: | JA7896-03: PSC Harmonics Tool
Description and instructions
This is used to carry out multiple frequency scans of a system using PowerFactory
Change Log | Person | Date | Version
Initial Version | David Mills (PSC) | 2020-05-26 | 1.0.0
Updated to include ConvexHull calculation | David Mills (PSC) | 2020-07-03 | 1.1.0
Updated to include specification of contingencies by line name | David Mills (PSC) | 2020-07-18 | 1.2.0

## Study_Settings
Study Settings
This sheet can be populated with settings to control some of the inputs and exports from the study that is about to be run. Some of these settings are configurable as part of the GUI
Results_Export_Folder | D:\Users\david\Desktop\ | Default folder to store log messages and the excel results, this can be overwritten using the GUI
Excel_Results | Results_ | Name of exported excel result file (unique time and date of the study is appended to end).
Pre_Case_Check | TRUE | True = Carries out a full check of the supplied cases and runs N-1 to see if they all solve in loadflow
Delete_Created_Folders | FALSE | True = Deletes the temporary folders created within PowerFactory after studies completed.
Export_to_Excel | TRUE | True = Export the results to Excel (If this isn't done then just runs pre-case checks)
Excel_Export_RX | TRUE | True = Exports the R & X data
Excel_Export_Z12 | FALSE | True = Exports the Mutual Impedance to excel
Include_Intact | TRUE | True = Will include an additional result for the intact system
Include_Loci | TRUE | True = Will calculate and produce the boundary points around the R/X data for each node at each harmonic (note only possible if Excel_Export_RX is also True and recommended to have frequency scan step size < nominal frequency)

## Base_Scenarios
Scenarios to Analyse
Name | Database | Studycase (.IntCase) | Operational Scenario (.IntScenario)
HighLoad | AEMO_VIC_V0_20200723 | High Load Case | HighLoadTap
MedLoad | AEMO_VIC_V0_20200723 | Medium Load Case | MediumLoadTap
LowLoad | AEMO_VIC_V0_20200723 | Low Load Case | LowLoadTap
Note on A4: Author: Enter name to be used on output files. Make this unique for each entry otherwise you won't be able to distinguish. Example SV Topology 1 No Caps WP Topology 5 with Caps
Note on B4: Author: Name of the database to activate
Note on C4: Author: Name of the Studycase to activate.
Note on D4: Author: Name of Operational Scenario to Activate

## Contingencies_Breakers
Contingencies (Breaker Operations) to Analyse
Contingency Analysis | Name of existing contingency analysis command that includes details of all of the contingencies to be considered (Set to FALSE if not using) | .ComSimoutage | FALSE
General | Breaker 1 |  |  | Breaker 2 |  |  | Breaker 3 |  |  | Breaker 4 |  |  | Breaker 5 |  |  | Breaker 6 |  |  | Breaker 7 |  |  | Breaker 8 |  |  | Breaker 9
Name | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status
CB Outage 1 | MOORABOOL 500KV | Switch_1196890 | Open
CB Outage 2 | KEILOR 500KV | Switch_209960 | Open | KEILOR 500KV | Switch_209961 | Open
Note on D3: Author: Either enter the name of a Contingency analysis in the study case (*.ComSimoutage) to use or set to False and use the contingencies described below
Note on B5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on C5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on E5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on F5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on H5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on I5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on K5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on L5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on N5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on O5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on Q5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on R5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on T5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on U5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on W5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on X5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on Z5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on AA5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'

## Contingencies_Lines
Contingencies (Line Outages) to Analyse
Contingency Analysis | Name of existing contingency analysis command that includes details of all of the contingencies to be considered (Set to FALSE if not using) | .ComSimoutage | FALSE
General | Line 1 |  | Line 2 |  | Line 3 |  | Line 4 |  | Line 5 |  | Line 6 |  | Line 7 |  | Line 8 |  | Line 9
Name | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status
Line 1 | 207466_MLTS_BATS 1 220kV | Out of Service
Line 2 | 207483_TTS_KTS_2A_T1-T7 | Out of Service
Line 3 | 1898316_DDTS_SHTS 220kV | Out of Service
Line 4 | 207444_HWPS_YPS_1 220kV | Out of Service
Line 5 | 207445_HWPS_YPS_2 220kV | Out of Service
Line 6 | 207447_TRTS_HYTS/APD 1 500kV | Out of Service
Line 7 | 207448_MOPS_HYTS/APD 2 500kV | Out of Service
Line 8 | 207449_FBTS_ BLTS 220kV | Out of Service
Line 9 | 207450_ATS_BLTS 220kV | Out of Service
Line 10 | 207452_KTS_BLTS 220kV | Out of Service
Note on D3: Author: Either enter the name of a Contingency analysis in the study case (*.ComSimoutage) to use or set to False and use the contingencies described below
Note on B5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on D5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on F5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on H5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on J5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on L5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on N5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on P5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on R5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)

## Terminals
Terminals to Analyse
NAMES OKAY
Name | Station | Terminal | Mutual
MOOR 220 | MOORABOOL 500KV | 201258_MLTS_7MN2 | FALSE
MOOR 500 | MOORABOOL 500KV | 201247_MLTS_6MN2 | FALSE
KEIL 220 | KEILOR 500KV | 201357_KTS_7MN2 | FALSE
KEIL 66 | KEILOR 500KV | 201337_KTS_3MN1 | FALSE
SMORANG 330 | SOUTH MORANG 500KV | 201288_SMTS_5MN2 | FALSE
SMORANG 500 | SOUTH MORANG 500KV | 201277_SMTS_6MN1 | FALSE
Note on A4: Author: Name of the station Must be unique in the column and have total length less than 19 characters
Note on B4: Author: Name of the station Example: Cauteen
Note on C4: Author: Name of the terminal in the station (.ElmTerm)
Note on D4: Author: If set to TRUE then mutual impedance will be calculated from this node to other nodes. Helps to improve study speed by setting to False

## Loadflow_Settings
Loadflow Settings
Study Case Load Flow Settings | Name of load flow settings to be used for studycase (enter FALSE to use settings below) | .ComLdf | Load Flow Calculation
Basic | Calculation method (0 Balanced AC, 1 Unbalanced AC, 2 DC) | ldf.iopt_net | 0
| Automatic Tap Adjustment | ldf.iopt_at | 1
| Automatic Shunt Adjustment | ldf.iopt_ashnt | 0
| Automatic Tap Adjustment of Phase Shifters | ldf.iPST_at | 0
| Consider Reactive Power Limits | ldf.iopt_lim | 1
| Consider Reactive Power Limits Scaling Factor | ldf.iopt_ashnt | 0
| Temperature Dependency: Line Cable Resistances (0 ...at 20C, 1 at Maximum Operational Temperature) | ldf.iopt_tem | 0
| Consider Voltage Dependency of Loads | ldf.iopt_pq | 0
| Feeder Load Scaling | ldf.iopt_fls | 0
| Consider Coincidence of Low-Voltage Loads | ldf.iopt_sim | 0
| Scaling Factor for Night Storage Heaters | ldf.scPnight | 100
Advanced Power Control | Active Power Control (0 as Dispatched, 1 According to Secondary Control, 2 Acording to Primary Control, 3 Acording to Inertias) | ldf.iopt_apdist | 0
| Consider Active Power Limits | ldf.iopt_plim | 1
| (0 Ref Machine, 1 Load, Static Gen, Dist slack by loads, Dist slack by Sync, | ldf.iPbalancing | 0
| Reference Busbar (NetElements\Substation\Terminal) | ldf.rembar
| Angle | ldf.phiini | 0
Advanced Options | Load Flow Method ( NR Current, 1 NR (Power Eqn Classic) | ldf.i_power | 1
| No Topology Rebuild | ldf.iopt_notopo | 1
| No initialisation | ldf.iopt_noinit | 0
| Consideration of transformer winding ratio | ldf.utr_init | 1
| Max Transformer Phase Shift | ldf.maxPhaseShift | 20
| Tap Adjustment ( 0 Direct, 1 Step) | ldf.itapopt | 0
| Min COntroller Relaxation Factor | ldf.krelax | 1
| Station Controller (0 Standard, 1 Gen HV, 2 Gen LV | ldf.iopt_stamode | 0
| Modelling Method of Towers (0 With In/ Output signals, 1 ignore couplings, 2 equation in lines) | ldf.iopt_igntow | 2
| Use this load flow for initialisation of OPF | ldf.initOPF | 0
| Zone Scaling ( 0 Consider all loads, 1 Consider adjustable loads only) | ldf.zoneScale | 1
Iteration Control | Max No Iterations for Newton-Raphson Iteration | ldf.itrlx | 25
| Max No Iterations for Outer Loop | ldf.ictrlx | 20
| Max No Iterations for Number of steps | ldf.nsteps | 1
| Max Acceptable Load Flow Error for Nodes | ldf.errlf | 1
| Max Acceptable Load Flow Error for Model Equations | ldf.erreq | 0.1
| Iteration Step Size ( 0 Automatic, 1 Fixed Relaxation) | ldf.iStepAdapt | 0
| If Fixed Relaxation factor | ldf.relax | 1
| Automatic Model Adaption for Convergence | ldf.iopt_lev | 0
Outputs | Show 'outer Loop' Messages | ldf.iShowOutLoopMsg | 1
| Show Convergence Progress Report | ldf.iopt_show | 1
| Number of reported buses/models per iteration | ldf.num_conv | 1
| Show verification report | ldf.iopt_check | 0
| Max Loading of Edge Element | ldf.loadmax | 80
| Lower Limit of Allowed Voltage | ldf.vlmin | 0.95
| Upper Limit of Allowed Voltage | ldf.vlmax | 1.05
| Check Control Conditions | ldf.iopt_chctr | 1
Load Generation Scaling | Load Scaling Factor | ldf.scLoadFac | 100
| Generation Scaling Factor | ldf.scGenFac | 100
| Motor Scaling Factor | ldf.scMotFac | 100
Low Voltage Analysis | Fixed Load kVA | ldf.Sfix | 0
| Power Factor of Fixed Load | ldf.cosfix | 0.9
| Max Power Per Customer kVA | ldf.Svar | 12
| Power Factor of Variable Part | ldf.cosvar | 0.95
| Coincidence Factor | ldf.ginf | 0.1
| Voltage Drop Analysis (0 Stochastic Evaluation, 1 Maximum Current Estimation) | ldf.i_volt | 0
Advanced Simulation Optns | Consider Protection Devices ( 0 None, 1 all, 2 Main, 3 Backup) | ldf.iopt_prot | 1
| Ignore Composite Elements | ldf.ign_comp | 0
Note on D4: Author: Either enter the name of the Load Flow command in the study case (typically "Load Flow Calculation.ComLdf") to use or set to False and populate the settings below.

## Frequency_Sweep
Frequency Sweep Settings
Study Case Frequency Sweep | Name of frequency scan settings to be used for studycase (enter FALSE to use settings below) | ComFsweep | Frequency Sweep
Basic | Nominal Frequency | frq.fnom | 50
| Network Representation (0=Balanced 1=Unbalanced) | frq.iopt_net | 0
| Impedance Calculation Start frequency | frq.fstart | 50
| Stop Frequency | frq.fstop | 500
| Step Size | frq.fstep | 50
| Automatic Step Size Adaption | frq.i_adapt | 0
Advanced | Setting for Step Size Adaption Maximum Prediction Error | frq.errmax | 0.01
| Minimum Prediction Error | frq.errinc | 0.005
| Step Size Increase Delay | frq.ninc | 10
| Calculate R, X at output frequency for all nodes | frq.ioutall | 0
Note on D4: Author: Either enter the name of the Frequency Sweep command in the study case (typically "Frequency Sweep.ComFsweep") to use or set to False and populate the settings below.
Note on D9: Author: If Include_Convex then recommended to have a value < nominal frequency.

## Loci_Settings
Loci Settings
Settings Applied to All Harmonic Orders |  |  | From Frequency_Sweep worksheet
Harmonic Impedance Polygon Range (+/- Hz) |  | 15 | Nominal Frequency (Hz) |  | 50
Harmonic Impedance Percentage to Exclude (%) |  | 0 | Frequency Scan Start Frequency (Hz) |  | 50
Maximum number of vertices |  | 10 | Frequency Scan Stop Frequency (Hz) |  | 500
Settings Applied to Individual Harmonic Orders
Harmonic Number | Harmonic Frequency (Hz) | Minimum Frequency (Hz) | Maximum Frequency (Hz) | Percentage to Exclude (%) | Maximum No. Vertices
2 | 100 | 75 | 125 | 5 | 10
3 | 150 | 125 | 175 | 5 | 10
4 | 200 | 175 | 225 | 5 | 10
5 | 250 | 225 | 275 | 5 | 10
6 | 300 | 275 | 325 | 5 | 10
7 | 350 | 325 | 375 | 5 | 10
8 | 400 | 375 | 425 | 5 | 10
9 | 450 | 425 | 475 | 5 | 10
10 | 500 | 475 | 525 | 5 | 10
11 | 550 | 525 | 575 | 5 | 10
12 | 600 | 575 | 625 | 5 | 10
13 | 650 | 625 | 675 | 5 | 10
14 | 700 | 675 | 725 | 5 | 10
15 | 750 | 725 | 775 | 5 | 10
16 | 800 | 775 | 825 | 5 | 10
17 | 850 | 825 | 875 | 5 | 10
18 | 900 | 875 | 925 | 5 | 10
19 | 950 | 925 | 975 | 5 | 10
20 | 1000 | 975 | 1025 | 5 | 10
21 | 1050 | 1025 | 1075 | 5 | 10
22 | 1100 | 1075 | 1125 | 5 | 10
23 | 1150 | 1125 | 1175 | 5 | 10
24 | 1200 | 1175 | 1225 | 5 | 10
25 | 1250 | 1225 | 1275 | 5 | 10
26 | 1300 | 1275 | 1325 | 5 | 10
27 | 1350 | 1325 | 1375 | 5 | 10
28 | 1400 | 1375 | 1425 | 5 | 10
29 | 1450 | 1425 | 1475 | 5 | 10
30 | 1500 | 1475 | 1525 | 5 | 10
31 | 1550 | 1525 | 1575 | 5 | 10
32 | 1600 | 1575 | 1625 | 5 | 10
33 | 1650 | 1625 | 1675 | 5 | 10
34 | 1700 | 1675 | 1725 | 5 | 10
35 | 1750 | 1725 | 1775 | 5 | 10
36 | 1800 | 1775 | 1825 | 5 | 10
37 | 1850 | 1825 | 1875 | 5 | 10
38 | 1900 | 1875 | 1925 | 5 | 10
39 | 1950 | 1925 | 1975 | 5 | 10
40 | 2000 | 1975 | 2025 | 5 | 10
41 | 2050 | 2025 | 2075 | 5 | 10
42 | 2100 | 2075 | 2125 | 5 | 10
43 | 2150 | 2125 | 2175 | 5 | 10
44 | 2200 | 2175 | 2225 | 5 | 10
45 | 2250 | 2225 | 2275 | 5 | 10
46 | 2300 | 2275 | 2325 | 5 | 10
47 | 2350 | 2325 | 2375 | 5 | 10
48 | 2400 | 2375 | 2425 | 5 | 10
49 | 2450 | 2425 | 2475 | 5 | 10
50 | 2500 | 2475 | 2525 | 5 | 10
51 | 2550 | 2525 | 2575 | 5 | 10
52 | 2600 | 2575 | 2625 | 5 | 10
53 | 2650 | 2625 | 2675 | 5 | 10
54 | 2700 | 2675 | 2725 | 5 | 10
55 | 2750 | 2725 | 2775 | 5 | 10
56 | 2800 | 2775 | 2825 | 5 | 10
57 | 2850 | 2825 | 2875 | 5 | 10
58 | 2900 | 2875 | 2925 | 5 | 10
59 | 2950 | 2925 | 2975 | 5 | 10
60 | 3000 | 2975 | 3025 | 5 | 10
61 | 3050 | 3025 | 3075 | 5 | 10
62 | 3100 | 3075 | 3125 | 5 | 10
63 | 3150 | 3125 | 3175 | 5 | 10
64 | 3200 | 3175 | 3225 | 5 | 10
65 | 3250 | 3225 | 3275 | 5 | 10
66 | 3300 | 3275 | 3325 | 5 | 10
67 | 3350 | 3325 | 3375 | 5 | 10
68 | 3400 | 3375 | 3425 | 5 | 10
69 | 3450 | 3425 | 3475 | 5 | 10
70 | 3500 | 3475 | 3525 | 5 | 10
71 | 3550 | 3525 | 3575 | 5 | 10
72 | 3600 | 3575 | 3625 | 5 | 10
73 | 3650 | 3625 | 3675 | 5 | 10
74 | 3700 | 3675 | 3725 | 5 | 10
75 | 3750 | 3725 | 3775 | 5 | 10
76 | 3800 | 3775 | 3825 | 5 | 10
77 | 3850 | 3825 | 3875 | 5 | 10
78 | 3900 | 3875 | 3925 | 5 | 10
79 | 3950 | 3925 | 3975 | 5 | 10
80 | 4000 | 3975 | 4025 | 5 | 10
81 | 4050 | 4025 | 4075 | 5 | 10
82 | 4100 | 4075 | 4125 | 5 | 10
83 | 4150 | 4125 | 4175 | 5 | 10
84 | 4200 | 4175 | 4225 | 5 | 10
85 | 4250 | 4225 | 4275 | 5 | 10
86 | 4300 | 4275 | 4325 | 5 | 10
87 | 4350 | 4325 | 4375 | 5 | 10
88 | 4400 | 4375 | 4425 | 5 | 10
89 | 4450 | 4425 | 4475 | 5 | 10
90 | 4500 | 4475 | 4525 | 5 | 10
91 | 4550 | 4525 | 4575 | 5 | 10
92 | 4600 | 4575 | 4625 | 5 | 10
93 | 4650 | 4625 | 4675 | 5 | 10
94 | 4700 | 4675 | 4725 | 5 | 10
95 | 4750 | 4725 | 4775 | 5 | 10
96 | 4800 | 4775 | 4825 | 5 | 10
97 | 4850 | 4825 | 4875 | 5 | 10
98 | 4900 | 4875 | 4925 | 5 | 10
99 | 4950 | 4925 | 4975 | 5 | 10
100 | 5000 | 4975 | 5025 | 5 | 10
Note on C5: Author: If some harmonic impedance values are excluded they may still end up inside the polygon if the number of vertices is not "Unlimited"