## Clonee 220 kV
Terminal | Clonee 220 kV |  | Terminal | Clonee 220 kV
Terminal Name | Clonee 220 kV |  | Terminal Name | Clonee 220 kV_Corduff 220 kV |  | Clonee 220 kV_Woodland 220 kV
Nom Voltage (kV) | 220 |  | Nom Voltage (kV) | 220 |  | 220
Study Case | step0 |  | Study Case | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.8217 | 12.9573 | 50 | 7.617 | 5.7105 | 6.5262 | 7.5388
100 | 21.2812 | 28.631 | 100 | 19.0673 | 15.1286 | 16.6617 | 18.2105
150 | 39.2144 | 42.3247 | 150 | 38.401 | 35.1803 | 35.3857 | 33.8671
200 | 11.1819 | 23.5599 | 200 | 10.5336 | 12.4619 | 10.1625 | 7.9176
250 | 20.2095 | 37.6874 | 250 | 17.1958 | 10.4759 | 11.2073 | 12.9284
300 | 55.6653 | 56.5053 | 300 | 54.9383 | 39.3582 | 38.7979 | 31.664
350 | 31.5774 | 48.2058 | 350 | 43.4833 | 17.0397 | 22.0148 | 13.1553
400 | 6.4253 | 59.2146 | 400 | 13.571 | 4.6193 | 3.5939 | 17.361
450 | 17.6505 | 72.7467 | 450 | 4.6027 | 2.0586 | 7.2068 | 25.9482
500 | 32.0701 | 86.2218 | 500 | 17.9687 | 9.3992 | 17.01 | 34.5333
550 | 54.1875 | 97.0077 | 550 | 42.6674 | 25.2278 | 32.8158 | 42.0294
600 | 73.3698 | 87.5173 | 600 | 74.0312 | 48.2873 | 47.4508 | 33.5167
650 | 46.3634 | 94.9412 | 650 | 62.1731 | 26.2069 | 29.6533 | 27.1255
700 | 21.5632 | 110.4555 | 700 | 48.6226 | 14.6813 | 17.5321 | 37.4116
750 | 5.9597 | 116.9568 | 750 | 26.6735 | 11.1592 | 7.4616 | 38.9702
800 | 11.0228 | 129.7233 | 800 | 18.559 | 8.5839 | 2.4627 | 45.469
850 | 17.5564 | 146.2386 | 850 | 12.8167 | 6.6207 | 4.095 | 56.8197
900 | 21.4386 | 148.4015 | 900 | 9.8549 | 4.8667 | 5.6279 | 55.9049
950 | 26.0993 | 158.1634 | 950 | 6.5493 | 2.8534 | 8.335 | 58.0577
1000 | 29.9458 | 167.3679 | 1000 | 4.2619 | 1.76 | 10.3661 | 61.4808
1050 | 33.2076 | 169.9832 | 1050 | 2.3285 | 1.0527 | 11.6191 | 60.4666
1100 | 36.9873 | 187.1185 | 1100 | 1.5003 | 0.64024 | 13.7862 | 68.7156
1150 | 40.5018 | 199.5125 | 1150 | 2.6191 | 1.6551 | 16.603 | 76.9155
1200 | 43.6331 | 207.6298 | 1200 | 4.1122 | 2.1711 | 17.4478 | 77.4255
1250 | 47.5535 | 230.2093 | 1250 | 5.8928 | 3.6333 | 21.0032 | 93.0045
1300 | 51.4674 | 254.5295 | 1300 | 7.6309 | 5.0772 | 25.1229 | 112.4686
1350 | 54.8397 | 270.3316 | 1350 | 9.2067 | 5.8907 | 27.1785 | 120.8009
1400 | 56.5264 | 243.8326 | 1400 | 10.4593 | 5.9929 | 27.9826 | 106.626
1450 | 59.2864 | 256.4287 | 1450 | 11.8584 | 5.9674 | 24.8708 | 94.7946
1500 | 64.05 | 286.9495 | 1500 | 13.981 | 8.4611 | 31.1925 | 122.0009
1550 | 68.3195 | 311.6978 | 1550 | 16.0637 | 10.6832 | 34.2896 | 134.6509
1600 | 73.9511 | 356.7126 | 1600 | 18.6862 | 14.745 | 41.696 | 171.9349
1650 | 78.0335 | 374.0144 | 1650 | 20.7455 | 16.8395 | 46.4657 | 189.8063
1700 | 82.4953 | 352.37 | 1700 | 23.3202 | 20.0208 | 59.179 | 214.2093
1750 | 76.6836 | 286.4934 | 1750 | 21.1833 | 10.1475 | 32.0533 | 99.8902
1800 | 85.2009 | 352.0904 | 1800 | 25.2674 | 15.8281 | 42.8147 | 147.6353
1850 | 89.4757 | 361.1734 | 1850 | 27.8455 | 18.3613 | 47.2605 | 157.544
1900 | 95.677 | 404.2261 | 1900 | 31.1589 | 22.0706 | 52.0409 | 181.121
1950 | 99.0982 | 409.0674 | 1950 | 33.2848 | 21.8823 | 52.2542 | 177.2386
2000 | 113.6601 | 544.3387 | 2000 | 41.3354 | 39.0402 | 74.1106 | 289.4046

## Corduff 220 kV
Terminal | Corduff 220 kV |  | Terminal | Corduff 220 kV
Terminal Name | Corduff 220 kV |  | Terminal Name | Corduff 220 kV_Clonee 220 kV |  | Corduff 220 kV_Woodland 220 kV
Nom Voltage (kV) | 220 |  | Nom Voltage (kV) | 220 |  | 220
Study Case | step0 |  | Study Case | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.1779 | 9.0457 | 50 | 7.617 | 5.7105 | 6.2255 | 5.7526
100 | 20.2787 | 22.3824 | 100 | 19.0673 | 15.1286 | 16.1803 | 15.3128
150 | 39.7371 | 43.1272 | 150 | 38.401 | 35.1803 | 35.7282 | 35.6883
200 | 11.1919 | 13.9875 | 200 | 10.5336 | 12.4619 | 11.1326 | 12.582
250 | 19.9812 | 26.0315 | 250 | 17.1958 | 10.4759 | 11.3971 | 10.6409
300 | 61.6037 | 92.5099 | 300 | 54.9383 | 39.3582 | 40.3225 | 41.0185
350 | 50.5811 | 48.6426 | 350 | 43.4833 | 17.0397 | 28.1548 | 17.6698
400 | 15.9459 | 14.7798 | 400 | 13.571 | 4.6193 | 7.8034 | 4.7707
450 | 5.2713 | 5.3623 | 450 | 4.6027 | 2.0586 | 2.9963 | 2.1259
500 | 20.281 | 21.6687 | 500 | 17.9687 | 9.3992 | 12.45 | 9.6649
550 | 47.9587 | 55.5832 | 550 | 42.6674 | 25.2278 | 30.2495 | 25.8282
600 | 84.1559 | 114.3554 | 600 | 74.0312 | 48.2873 | 51.2915 | 49.3769
650 | 72.0937 | 73.0063 | 650 | 62.1731 | 26.2069 | 39.0023 | 26.6535
700 | 56.4982 | 48.3793 | 700 | 48.6226 | 14.6813 | 29.008 | 15.133
750 | 30.3927 | 28.565 | 750 | 26.6735 | 11.1592 | 17.3497 | 11.3962
800 | 20.9169 | 20.2196 | 800 | 18.559 | 8.5839 | 12.6019 | 8.735
850 | 14.2069 | 13.988 | 850 | 12.8167 | 6.6207 | 9.2754 | 6.7121
900 | 11.1157 | 11.0294 | 900 | 9.8549 | 4.8667 | 6.9822 | 4.9139
950 | 7.4246 | 7.3502 | 950 | 6.5493 | 2.8534 | 4.2674 | 2.8662
1000 | 4.8517 | 4.8228 | 1000 | 4.2619 | 1.76 | 2.7097 | 1.7738
1050 | 2.6357 | 2.6321 | 1050 | 2.3285 | 1.0527 | 1.5227 | 1.0567
1100 | 1.6997 | 1.7016 | 1100 | 1.5003 | 0.64024 | 0.95335 | 0.63631
1150 | 2.8243 | 2.8286 | 1150 | 2.6191 | 1.6551 | 2.028 | 1.6341
1200 | 4.5457 | 4.5628 | 1200 | 4.1122 | 2.1711 | 2.8459 | 2.1292
1250 | 6.3564 | 6.3723 | 1250 | 5.8928 | 3.6333 | 4.4473 | 3.5472
1300 | 8.1079 | 8.1174 | 1300 | 7.6309 | 5.0772 | 6.0854 | 4.9348
1350 | 9.8124 | 9.8294 | 1350 | 9.2067 | 5.8907 | 7.1768 | 5.699
1400 | 11.4011 | 11.4398 | 1400 | 10.4593 | 5.9929 | 8.1577 | 5.7636
1450 | 13.1245 | 13.2361 | 1450 | 11.8584 | 5.9674 | 7.856 | 5.7213
1500 | 14.9954 | 15.0286 | 1500 | 13.981 | 8.4611 | 10.4871 | 8.0517
1550 | 16.9666 | 16.9577 | 1550 | 16.0637 | 10.6832 | 12.4329 | 10.1211
1600 | 19.138 | 19.0012 | 1600 | 18.6862 | 14.745 | 15.8694 | 13.8507
1650 | 21.0881 | 20.8121 | 1650 | 20.7455 | 16.8395 | 18.2507 | 15.7613
1700 | 23.1058 | 22.1366 | 1700 | 23.3202 | 20.0208 | 24.0287 | 18.5481
1750 | 23.7475 | 24.0815 | 1750 | 21.1833 | 10.1475 | 13.6207 | 9.3583
1800 | 26.8278 | 26.7318 | 1800 | 25.2674 | 15.8281 | 18.7887 | 14.4701
1850 | 29.3182 | 29.0464 | 1850 | 27.8455 | 18.3613 | 21.6382 | 16.6898
1900 | 32.2935 | 31.8542 | 1900 | 31.1589 | 22.0706 | 24.4847 | 19.8622
1950 | 34.8159 | 34.4517 | 1950 | 33.2848 | 21.8823 | 25.0892 | 19.7402
2000 | 40.5148 | 39.3336 | 2000 | 41.3354 | 39.0402 | 37.0601 | 34.9025

## Woodland 220 kV
Terminal | Woodland 220 kV |  | Terminal | Woodland 220 kV
Terminal Name | Woodland 220 kV |  | Terminal Name | Woodland 220 kV_Clonee 220 kV |  | Woodland 220 kV_Corduff 220 kV
Nom Voltage (kV) | 220 |  | Nom Voltage (kV) | 220 |  | 220
Study Case | step0 |  | Study Case | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 7.3678 | 7.613 | 50 | 6.5262 | 7.5388 | 6.2255 | 5.7526
100 | 18.1523 | 18.4732 | 100 | 16.6617 | 18.2105 | 16.1803 | 15.3128
150 | 35.1892 | 34.3974 | 150 | 35.3857 | 33.8671 | 35.7282 | 35.6883
200 | 8.6121 | 8.0828 | 200 | 10.1625 | 7.9176 | 11.1326 | 12.582
250 | 12.8662 | 13.4798 | 250 | 11.2073 | 12.9284 | 11.3971 | 10.6409
300 | 36.8096 | 32.9328 | 300 | 38.7979 | 31.664 | 40.3225 | 41.0185
350 | 9.4145 | 13.5904 | 350 | 22.0148 | 13.1553 | 28.1548 | 17.6698
400 | 11.468 | 17.9021 | 400 | 3.5939 | 17.361 | 7.8034 | 4.7707
450 | 20.2363 | 26.7642 | 450 | 7.2068 | 25.9482 | 2.9963 | 2.1259
500 | 29.7132 | 35.5495 | 500 | 17.01 | 34.5333 | 12.45 | 9.6649
550 | 40.8815 | 43.0817 | 550 | 32.8158 | 42.0294 | 30.2495 | 25.8282
600 | 40.9982 | 34.367 | 600 | 47.4508 | 33.5167 | 51.2915 | 49.3769
650 | 16.8485 | 27.7395 | 650 | 29.6533 | 27.1255 | 39.0023 | 26.6535
700 | 17.5483 | 38.1266 | 700 | 17.5321 | 37.4116 | 29.008 | 15.133
750 | 22.5653 | 39.6915 | 750 | 7.4616 | 38.9702 | 17.3497 | 11.3962
800 | 28.0995 | 46.2529 | 800 | 2.4627 | 45.469 | 12.6019 | 8.735
850 | 35.5654 | 57.557 | 850 | 4.095 | 56.8197 | 9.2754 | 6.7121
900 | 37.4509 | 56.3685 | 900 | 5.6279 | 55.9049 | 6.9822 | 4.9139
950 | 39.8016 | 58.2952 | 950 | 8.335 | 58.0577 | 4.2674 | 2.8662
1000 | 42.7478 | 61.5031 | 1000 | 10.3661 | 61.4808 | 2.7097 | 1.7738
1050 | 43.7703 | 60.3197 | 1050 | 11.6191 | 60.4666 | 1.5227 | 1.0567
1100 | 48.2564 | 68.2541 | 1100 | 13.7862 | 68.7156 | 0.95335 | 0.63631
1150 | 54.1637 | 75.9457 | 1150 | 16.603 | 76.9155 | 2.028 | 1.6341
1200 | 54.3541 | 75.9905 | 1200 | 17.4478 | 77.4255 | 2.8459 | 2.1292
1250 | 62.6508 | 90.9386 | 1250 | 21.0032 | 93.0045 | 4.4473 | 3.5472
1300 | 72.6071 | 109.338 | 1300 | 25.1229 | 112.4686 | 6.0854 | 4.9348
1350 | 76.7264 | 116.8493 | 1350 | 27.1785 | 120.8009 | 7.1768 | 5.699
1400 | 76.6149 | 102.4987 | 1400 | 27.9826 | 106.626 | 8.1577 | 5.7636
1450 | 66.4472 | 90.8176 | 1450 | 24.8708 | 94.7946 | 7.856 | 5.7213
1500 | 81.2057 | 116.0034 | 1500 | 31.1925 | 122.0009 | 10.4871 | 8.0517
1550 | 86.956 | 127.7385 | 1550 | 34.2896 | 134.6509 | 12.4329 | 10.1211
1600 | 103.1195 | 161.6476 | 1600 | 41.696 | 171.9349 | 15.8694 | 13.8507
1650 | 113.1779 | 177.6165 | 1650 | 46.4657 | 189.8063 | 18.2507 | 15.7613
1700 | 140.966 | 198.438 | 1700 | 59.179 | 214.2093 | 24.0287 | 18.5481
1750 | 74.6598 | 92.1355 | 1750 | 32.0533 | 99.8902 | 13.6207 | 9.3583
1800 | 97.5738 | 134.9977 | 1800 | 42.8147 | 147.6353 | 18.7887 | 14.4701
1850 | 105.0309 | 143.1998 | 1850 | 47.2605 | 157.544 | 21.6382 | 16.6898
1900 | 113.2283 | 163.0739 | 1900 | 52.0409 | 181.121 | 24.4847 | 19.8622
1950 | 112.7991 | 159.8184 | 1950 | 52.2542 | 177.2386 | 25.0892 | 19.7402
2000 | 155.161 | 258.6115 | 2000 | 74.1106 | 289.4046 | 37.0601 | 34.9025