## Cover Sheet
Harmonic Automated Simulation Tool (HAST) Input Spreadsheet
Description
This is used to carry out stage 1 & 2 harmonic analysis
Change Log | Person | Date | Version
Created | Barry O'Connell | 2016-12-01 | v1
1) Create results files based on whether mutual was chosen or not. Improve sim time for when not necessary. 2) Updated filter to not skip graphing if more than 255 series excel error returned. 3) Added more timing tags in post processing to progress log to analyse performance 4) Added an ".ElmTerm" to the filter to mitigate bug when the sub station and terminal have been named the same. 5) Fixed bug when mutual elements are not created the script does not try to delete the folder at the end. | Barry O'Connell | 2016-12-21 | v1.1
1) Added in Functionality for switching breakers open. | Barry O'Connell | 2017-04-24 | v1.2
1) Added in Functionality to run studies with a range of filter options | David Mills (PSC) | 20/20/2019 | v2.0

## Study_Settings
Study Settings
Recommended Settings
|  |  | Pre Stage | Stage 1 | Stage 2
Results_Export_Folder | C:\Users\david\Desktop\ | Folder to store logs (progress/error) and the excel results, if blank it uses the current working directory ie where the script is stored.
Excel_Results | Results_ | Name of exported excel result file (python adds on the unique time and date).
Progress_Log | Progress_Log_ | Name for progress log file (python adds on the unique time and date)
Error_Log | Error_Log_ | Name for error file. This is only created if there is and error (python adds on the unique time and date).
Net_Elm | EirGrid.ElmNet | The name of the network elements in PowerFactory. Note this is Case sensitive.
Mut_Elm_Fld | ElmMut | Name of the folder to create under the network elements to store mutual impedances between terminals. (python adds on the unique time and date).
Results_Folder | Results_ | Name of the folder created to keep results (.ElmRes). This is stored under the active studycase. (python adds on the unique time and date).
Operation_Scenario_Folder | Op_Scenarios_ | Name of the folder created to store Operational Scenarios (python adds on the unique time and date).
Pre_Case_Check | TRUE | True = Carries out a full check of the supplied cases and runs N-1 to see if they all solve in loadflow
FS_Sim | TRUE | True = Carries out the frequency sweep
HRM_Sim | FALSE | True = Carries out the Harmonic Load flow
Skip_Unsolved_Ldf | FALSE | True = Skips attempting unsolved Load Flow cases in either Freq or Harm analysis
Delete_Created_Folders | TRUE | True = Deletes the 3 created folder after 1) Results under studcases, 2)Operation Scenarios, 3) Mutual Element Folder under network elements
Export_to_Excel | TRUE | True = Export the results to Excel
Excel_Visible | FALSE | True = Makes Excel Visible while plotting. Can be annoying if you are doing other work as if you click the excel screen it stops the simulation
Excel_Export_RX | FALSE | True = Exports the R & X data
Excel_Convex_Hull | FALSE | True = Calculates the Convex Hull of the RX points and exports the data and adds it to the graph
Excel_Export_Z | TRUE | True = Exports the Self Impedance to excel
Excel_Export_Z12 | TRUE | True = Exports the Mutual Impedance to excel
Excel_Export_HRM | FALSE | True = Export Mutual Impedances to excel
Note on A5: Author: Leave it blank it will use the current working directory the script is in. If you want to export the results to a specific folder then enter it C:\Users\oconnell_b\Desktop\Scrap\

## Base_Scenarios
Scenarios to Analyse
Name | Database | Studycase (.IntCase) | Operational Scenario (.IntScenario)
SC1 | AIM 2017-MODEL-07022019-TAP_TEST | BC_CustDevs_CLOph3 | SV 2.5GW E-250 M0 W1350
Note on A4: Author: Enter name to be used on output files. Make this unique for each entry otherwise you won't be able to distinguish. Example SV Topology 1 No Caps WP Topology 5 with Caps
Note on B4: Author: Name of the database to activate
Note on C4: Author: Name of the Studycase to activate.
Note on D4: Author: Name of Operational Scenario to Activate

## Contingencies
Contingencies to Analyse
| Breaker 1 |  |  | Breaker 2 |  |  | Breaker 3 |  |  | Breaker 4 |  |  | Breaker 5 |  |  | Breaker 6 |  |  | Breaker 7 |  |  | Breaker 8 |  |  | Breaker 9
Name | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status
Base_Case | 0
CLO2-CDU2-ckt1 | Clonee | 220 kV Corduff CB | Open | Corduff | 220 kV Clonee CB | Open

## Terminals
Terminals to Analyse
Name | Station | Terminal | Mutual
Bracetown 220 kV | Bracetown | 220 kV A2 | TRUE
Clonee 220 kV | Clonee | 220 kV A1 | TRUE
Note on A4: Author: Name of the station Must be unique in the column
Note on B4: Author: Name of the station Example: Cauteen
Note on C4: Author: Name of the terminal in the station (.ElmTerm)
Note on D4: Author: If set to TRUE then mutual impedance will be calculated from this node to other nodes. Helps to improve study speed by setting to False

## Filters
Filters to Include
Only a single filter will be included at a time
Filter Name | Station | Terminal | Type | Reactive Power Start | Reactive Power End | Number of Steps | Resonant Frequency Start | Resonant Frequency Stop | Number of Steps | Quality Factor | Parallel Resistance (Ohms)
Note on A4: Author: Name of the station Must be unique in the column
Note on B4: Author: Name of the station Example: Cauteen
Note on C4: Author: Name of the terminal in the station (.ElmTerm)
Note on D4: Author: Name of the terminal in the station (.ElmTerm)
Note on E4: Author: If set to TRUE then mutual impedance will be calculated from this node to other nodes. Helps to improve study speed by setting to False

## Loadflow_Settings
Loadflow Settings
Basic | Calculation method (0 Balanced AC, 1 Unbalanced AC, 2 DC) | ldf.iopt_net | 0
| Automatic Tap Adjustment | ldf.iopt_at | 1
| Automatic Shunt Adjustment | ldf.iopt_ashnt | 1
| Consider Reactive Power Limits | ldf.iopt_lim | 1
| Consider Reactive Power Limits Scaling Factor | ldf.iopt_ashnt | 1
| Temperature Dependency: Line Cable Resistances (0 ...at 20C, 1 at Maximum Operational Temperature) | ldf.iopt_tem | 0
| Consider Voltage Dependency of Loads | ldf.iopt_pq | 1
| Feeder Load Scaling | ldf.iopt_fls | 1
| Consider Coincidence of Low-Voltage Loads | ldf.iopt_sim | 0
| Scaling Factor for Night Storage Heaters | ldf.scPnight | 100
Advanced Power Control | Active Power Control (0 as Dispatched, 1 According to Secondary Control, 2 Acording to Primary Control, 3 Acording to Inertias) | ldf.iopt_apdist | 1
| Consider Active Power Limits | ldf.iopt_plim | 1
| (0 Ref Machine, 1 Load, Static Gen, Dist slack by loads, Dist slack by Sync, | ldf.iPbalancing | 0
| Reference Busbar | ldf.rembar | EIRGRID\Turlough Hill\220 kV T2001/2 TCB.ElmTerm
| Angle | ldf.phiini | 0
Advanced Options | Load Flow Method ( NR Current, 1 NR (Power Eqn Classic) | ldf.i_power | 0
| No Topology Rebuild | ldf.iopt_notopo | 0
| No initialisation | ldf.iopt_noinit | 0
| Consideration of transformer winding ratio | ldf.utr_init | 1
| Max Transformer Phase Shift | ldf.maxPhaseShift | 20
| Tap Adjustment ( 0 Direct, 1 Step) | ldf.itapopt | 0
| Min COntroller Relaxation Factor | ldf.krelax | 1
| Station Controller (0 Standard, 1 Gen HV, 2 Gen LV | ldf.iopt_stamode | 0
| Modelling Method of Towers (0 With In/ Output signals, 1 ignore couplings, 2 equation in lines) | ldf.iopt_igntow | 2
| Use this load flow for initialisation of OPF | ldf.initOPF | 0
| Zone Scaling ( 0 Consider all loads, 1 Consider adjustable loads only) | ldf.zoneScale | 0
Iteration Control | Max No Iterations for Newton-Raphson Iteration | ldf.itrlx | 100
| Max No Iterations for Outer Loop | ldf.ictrlx | 80
| Max No Iterations for Number of steps | ldf.nsteps | 5
| Max Acceptable Load Flow Error for Nodes | ldf.errlf | 10000
| Max Acceptable Load Flow Error for Model Equations | ldf.erreq | 10
| Iteration Step Size ( 0 Automatic, 1 Fixed Relaxation) | ldf.iStepAdapt | 1
| If Fixed Relaxation factor | ldf.relax | 1
| Automatic Model Adaption for Convergence | ldf.iopt_lev | 1
Outputs | Show 'outer Loop' Messages | ldf.iShowOutLoopMsg | 0
| Show Convergence Progress Report | ldf.iopt_show | 1
| Number of reported buses/models per iteration | ldf.num_conv | 2
| Show verification report | ldf.iopt_check | 1
| Max Loading of Edge Element | ldf.loadmax | 110
| Lower Limit of Allowed Voltage | ldf.vlmin | 0.9
| Upper Limit of Allowed Voltage | ldf.vlmax | 1.12
| Output | #ldf.outcmd | ldf
| Check Control Conditions | ldf.iopt_chctr | 1
| Command | ldf.chkcmd | cmd
Load Generation Scaling | Load Scaling Factor | ldf.scLoadFac | 100
| Generation Scaling Factor | ldf.scGenFac | 100
| Motor Scaling Factor | ldf.scMotFac | 100
Low Voltage Analysis | Fixed Load kVA | ldf.Sfix | 0
| Power Factor of Fixed Load | ldf.cosfix | 0.9
| Max Power Per Customer kVA | ldf.Svar | 12
| Power Factor of Variable Part | ldf.cosvar | 0.95
| Coincidence Factor | ldf.ginf | 0.1
| Voltage Drop Analysis (0 Stochastic Evaluation, 1 Maximum Current Estimation) | ldf.i_volt | 1
Advanced Simulation Optns | Consider Protection Devices ( 0 None, 1 all, 2 Main, 3 Backup) | ldf.iopt_prot | 1
| Ignore Composite Elements | ldf.ign_comp | 1

## Frequency_Sweep
Frequency Sweep Settings
Basic | Nominal Frequency | nomfreq | 50
| Maximum Frequency | maxfrq | 2000
| Network Representation (0=Balanced 1=Unbalanced) | frq.iopt_net | 0
| Impedance Calculation Start frequency | frq.fstart | 50
| Stop Frequency | frq.fstop | 2025
| Step Size | frq.fstep | 5
| Automatic Step Size Adaption | frq.i_adapt | 0
| Nominal Frequency | frq.frnom | 50
| Output Frequency | frq.fshow | 2000
| Harmonic Order | frq.ifshow | 40
| Results Variable | frq.p_resvar | results
| Load flow | frq.cbutldf | ldf
Advanced | Setting for Step Size Adaption Maximum Prediction Error | frq.errmax | 0.01
| Minimum Prediction Error | frq.errinc | 0.005
| Step Size Increase Delay | frq.ninc | 10
| Calculate R, X at output frequency for all nodes | frq.ioutall | 0

## Harmonic_Loadflow
Harmonic Loadflow Settings
| Calculation method (0 Balanced AC, 1 Unbalanced AC) | hldf.iopt_net | 0
| Calculate Harmonic Load Flow 0 - Single Frequency 1 - All Frequencies | hldf.iopt_allfrq | 1
| Calculate Flicker | hldf.iopt_flicker | 0
| Calculate Sk at Fundamental Frequency | hldf.iopt_SkV | 0
| Nominal Frequency | hldf.frnom | 50
| Output Frequency | hldf.fshow | 150
| Harmonic Order | hldf.ifshow | 3
| Results Variable | #hldf.p_resvar | harm
| Load flow | #hldf.cbutldf | ldf
IEC 61000-3-6 | Treatment of Harmonic Sources | hdlf.iopt_harmsrc | 0
Advanced Options | Calculate HD and THD 0 Based on Fundamental Frequency values 1 Based on rated voltage/current | hldf.iopt_thd | 0
| Max Harmonic order for calculation of THD and THF | hldf.maxHrmOrder | 3
| Calculate Harmonic Factor ( HF) | hldf.iopt_HF | 0
| Calculate R, X at output frequency for all nodes | hldf.ioutall | 0
| Calculation of Factor-K (BS 7821) for Transformers | hldf.expQ | 1.6