## Cover Sheet
PSC Harmonics Input Spreadsheet
Reference Document: | JA7896-03: PSC Harmonics Tool
Description and instructions
This is used to carry out multiple frequency scans of a system using PowerFactory
Change Log | Person | Date | Version
Initial Version | David Mills (PSC) | 2020-05-26 | 1.0.0
Updated to include ConvexHull calculation | David Mills (PSC) | 2020-07-03 | 1.1.0
Updated to include specification of contingencies by line name | David Mills (PSC) | 2020-07-18 | 1.2.0

## Study_Settings
Study Settings
This sheet can be populated with settings to control some of the inputs and exports from the study that is about to be run. Some of these settings are configurable as part of the GUI
Results_Export_Folder | C:\Users\NegarShams\OneDrive - Power Systems Consultants Inc\Negar\___EirGrid_CapitalProject\With_LF_40_BC\ | Default folder to store log messages and the excel results, this can be overwritten using the GUI
Excel_Results | Results_ | Name of exported excel result file (unique time and date of the study is appended to end).
Pre_Case_Check | TRUE | True = Carries out a full check of the supplied cases and runs N-1 to see if they all solve in loadflow
Delete_Created_Folders | FALSE | True = Deletes the temporary folders created within PowerFactory after studies completed.
Export_to_Excel | TRUE | True = Export the results to Excel (If this isn't done then just runs pre-case checks)
Excel_Export_RX | TRUE | True = Exports the R & X data
Excel_Export_Z12 | FALSE | True = Exports the Mutual Impedance to excel
Include_Intact | TRUE | True = Will include an additional result for the intact system
Include_Loci | TRUE | True = Will calculate and produce the boundary points around the R/X data for each node at each harmonic (note only possible if Excel_Export_RX is also True and recommended to have frequency scan step size < nominal frequency)

## Base_Scenarios
Scenarios to Analyse
Name | Database | Studycase (.IntCase) | Operational Scenario (.IntScenario)
SV | JI7867_CP966 Phase B_N4_BC | SV | SV
WP_HW | JI7867_CP966 Phase B_N4_BC | WP-HW | WP-HW
Note on A4: Author: Enter name to be used on output files. Make this unique for each entry otherwise you won't be able to distinguish. Example SV Topology 1 No Caps WP Topology 5 with Caps
Note on B4: Author: Name of the database to activate
Note on C4: Author: Name of the Studycase to activate.
Note on D4: Author: Name of Operational Scenario to Activate

## Contingencies_Breakers
Contingencies (Breaker Operations) to Analyse
Contingency Analysis | Name of existing contingency analysis command that includes details of all of the contingencies to be considered (Set to FALSE if not using) | .ComSimoutage | FALSE
General | Breaker 1 |  |  | Breaker 2 |  |  | Breaker 3 |  |  | Breaker 4 |  |  | Breaker 5 |  |  | Breaker 6 |  |  | Breaker 7 |  |  | Breaker 8 |  |  | Breaker 9
Name | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status | Station | Breaker Name | Status
CDU2-CDU1-1 | Corduff | 220 kV T2101 DA | Open | Corduff | 110 kV T2101 DA | Open
CDU2-CDU1-2 | Corduff | 220 kV T2102 DA | Open | Corduff | 110 kV T2102 DA | Open
CLN4-CLN1B-1 | Coolnabacky | 400 kV T4201 DB | Open | Coolnabacky | 110 kV T4201 DA | Open | Coolnabacky | 110 kV K1-2 CB | Close
DSN4-DSN2-1 | Dunstown | 400 kV T4201 DB | Open | Dunstown | 220 kV T4201 DA | Open
DSN4-DSN2-2 | Dunstown | 400 kV T4202 DB | Open | Dunstown | 220 kV T4202 DA | Open
MAY2A-MAY1A-1 | Maynooth | 220 kV T2103 DA | Open | Maynooth | 110 kV T2103 DB | Open | Maynooth | 220 kV K1-2 CB | Close
MAY2A-MAY1A-2 | Maynooth | 220 kV T2104 DA | Open | Maynooth | 110 kV T2104 DB | Open | Maynooth | 220 kV K1-2 CB | Close
MAY2B-MAY1B-1 | Maynooth | 220 kV T2101 DB | Open | Maynooth | 110 kV T2101 DA | Open | Maynooth | 220 kV K1-2 CB | Close
MAY2B-MAY1B-2 | Maynooth | 220 kV T2102 DB | Open | Maynooth | 110 kV T2102 DA | Open | Maynooth | 220 kV K1-2 CB | Close
OST4-OST2-1 | Oldstreet | 400 kV T4202 DA | Open | Oldstreet | 220 kV T4202 DA | Open
WOO4-WOO2A-1 | Woodland | 400 kV T4201 DB | Open | Woodland | 220 kV T4201 DA | Open | Woodland | 220 kV T4202 CB | Close
WOO4-WOO2B-1 | Woodland | 400 kV T4202 DB | Open | Woodland | 220 kV T4202 DA | Open | Woodland | 220 kV T4202 CB | Close
WOO4-WOO2C-1 | Woodland | 400 kV T4204 DB | Open | Woodland | 220 kV T4204 DA | Open | Woodland | 220 kV T4202 CB | Close
PRN4-Fshunt-1 | Portan | 400 kV HP58 DA | Open
CTB2-MAYA2A-1 | Maynooth | 220 kV K1-2 CB | Close
CTB2-MAYA2B-1 | Maynooth | 220 kV K1-2 CB | Close
DSN2-MAY2B-1 | Maynooth | 220 kV K1-2 CB | Close
INT2-MAY2A-1 | Maynooth | 220 kV K1-2 CB | Close
MAY2A-SH2-1 | Maynooth | 220 kV K1-2 CB | Close
MAY2B-GOR2-1 | Maynooth | 220 kV K1-2 CB | Close
MAY2B-TH2-1 | Maynooth | 220 kV K1-2 CB | Close
CKM2-SSHUNT-1 | Carrickmines | 220 kV GIS R2001 CB | Open
PB2B-Sshunt | Poolbeg | 220 kV R2001 DB | Open
DSN4-WOO4-1 | Dunstown | 400 kV Woodland CB | Open | Woodland | 400 kV Dunstown CB(1) | Open
Note on D3: Author: Either enter the name of a Contingency analysis in the study case (*.ComSimoutage) to use or set to False and use the contingencies described below
Note on B5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on C5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on E5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on F5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on H5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on I5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on K5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on L5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on N5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on O5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on Q5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on R5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on T5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on U5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on W5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on X5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'
Note on Z5: Author: Name of PowerFactory element for substation with ending '.ElmSwitch'
Note on AA5: Author: Name of PowerFactory element in substation that has ending '.ElmCoup'

## Contingencies_Lines
Contingencies (Line Outages) to Analyse
Contingency Analysis | Name of existing contingency analysis command that includes details of all of the contingencies to be considered (Set to FALSE if not using) | .ComSimoutage | FALSE
General | Line 1 |  | Line 2 |  | Line 3 |  | Line 4 |  | Line 5 |  | Line 6 |  | Line 7 |  | Line 8 |  | Line 9
Name | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status | Line / Branch Name | Status
BEL2-FIN2A-1 | Belcamp - Finglas 220 kV | Out of Service
BEL2-SHL2-1 | Shellybanks - Belcamp 220 kV | Out of Service
CDU2A-FIN2A-1 | Corduff - Finglas #1 220 kV | Out of Service
CDU2A-HUN2B-1 | Corduff - Huntstown 220 kV | Out of Service
CDU2A-WOO2A-1 | Corduff - Woodland 220 kV S2 | Out of Service
CDU2A-CLE2-1 | Clonee - Corduff 220 kV S1 | Out of Service
CDU2A-CRU2-1 | Corduff - Cruiserath #1 220 kV | Out of Service
CKM2-DSN2-1 | Carrickmines - Dunstown 220 kV S3 | Out of Service
CLN4-MP4-1 | Dunstown - Moneypoint 400 kV S2 | Out of Service
CTB2-MAYA2A-1 | Inchicore - Maynooth #2 220 kV S3 | Out of Service
CTB2-MAYA2B-1 | Inchicore - Maynooth #1 220 kV S3 | Out of Service
DSN2-KLS2-1 | Dunstown - Kellis 220 kV S1 | Out of Service
DSN2-MAY2A-1 | Dunstown - Maynooth #2 220 kV S1 | Out of Service
DSN2-MAY2B-1 | Dunstown - Maynooth #1 220 kV S1 | Out of Service
DSN2-TH2-1 | Dunstown - Turlough Hill 220 kV S1 | Out of Service
DSN4-CLN4-1 | Dunstown - Coolnebacky 400 kV S2 | Out of Service
DSN4-WOO4-1 | Woodland - Dunstown 400 kV Cbl2 | Out of Service
FIN2A-HUN2A-1 | Finglas - Huntstown 220 kV | Out of Service
FIN2B-NW2-1 | Finglas - North Wall 220 kV | Out of Service
INT2-MAY2A-1 | Maynooth - Intel 220 kV | Out of Service
MAY2A-SH2-1 | Maynooth - Shannonbridge 220 kV S2 | Out of Service
MAY2B-GOR2-1 | Gorman - Maynooth 220 kV | Out of Service
MAY2B-TH2-1 | Maynooth - Turlough Hill 220 kV S4 | Out of Service
NW2-PB2B-1 | North Wall - Poolbeg 220 kV | Out of Service
OST4-MP4-1 | Moneypoint - Oldstreet 400 kV S2 | Out of Service
OST4-WOO4-1 | Oldstreet - Woodland 400 kV | Out of Service
WOO2-CLE2-1 | Clonee - Woodland 220 kV S1 | Out of Service
WOO2-INT2-1 | Woodland - Intel 220 kV | Out of Service
WOO4-PRN4-1 | Portan - Woodland 400 kV | Out of Service
WOO4-TLE4-1 | Woodland - Turleenan 400 kV | Out of Service
Note on D3: Author: Either enter the name of a Contingency analysis in the study case (*.ComSimoutage) to use or set to False and use the contingencies described below
Note on B5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on D5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on F5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on H5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on J5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on L5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on N5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on P5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)
Note on R5: Author: Element in PowerFactory of either type line (.ElmLne) or type branch (ElmBranch)

## Terminals
Terminals to Analyse
NAMES OKAY
Name | Station | Terminal | Mutual
Wood_B1 | Woodland | 400 kV B1 | FALSE
Wood_B2 | Woodland | 400 kV B2 | FALSE
Dunstown_B1 | Dunstown | 400 kV B1 | FALSE
Dunstown_B2 | Dunstown | 400 kV B2 | FALSE
Wood_B1_L | Woodland | 220 kV A1 | FALSE
Wood_B2_L | Woodland | 220 kV A2 | FALSE
Dunstown_B1_L | Dunstown | 220 kV A1 | FALSE
Dunstown_B2_L | Dunstown | 220 kV A2 | FALSE
Note on A4: Author: Name of the station Must be unique in the column and have total length less than 19 characters
Note on B4: Author: Name of the station Example: Cauteen
Note on C4: Author: Name of the terminal in the station (.ElmTerm)
Note on D4: Author: If set to TRUE then mutual impedance will be calculated from this node to other nodes. Helps to improve study speed by setting to False

## Loadflow_Settings
Loadflow Settings
Study Case Load Flow Settings | Name of load flow settings to be used for studycase (enter FALSE to use settings below) | .ComLdf | Load Flow Calculation
Basic | Calculation method (0 Balanced AC, 1 Unbalanced AC, 2 DC) | ldf.iopt_net | 0
| Automatic Tap Adjustment | ldf.iopt_at | 1
| Automatic Shunt Adjustment | ldf.iopt_ashnt | 0
| Automatic Tap Adjustment of Phase Shifters | ldf.iPST_at | 0
| Consider Reactive Power Limits | ldf.iopt_lim | 1
| Consider Reactive Power Limits Scaling Factor | ldf.iopt_ashnt | 0
| Temperature Dependency: Line Cable Resistances (0 ...at 20C, 1 at Maximum Operational Temperature) | ldf.iopt_tem | 0
| Consider Voltage Dependency of Loads | ldf.iopt_pq | 0
| Feeder Load Scaling | ldf.iopt_fls | 0
| Consider Coincidence of Low-Voltage Loads | ldf.iopt_sim | 0
| Scaling Factor for Night Storage Heaters | ldf.scPnight | 100
Advanced Power Control | Active Power Control (0 as Dispatched, 1 According to Secondary Control, 2 Acording to Primary Control, 3 Acording to Inertias) | ldf.iopt_apdist | 0
| Consider Active Power Limits | ldf.iopt_plim | 1
| (0 Ref Machine, 1 Load, Static Gen, Dist slack by loads, Dist slack by Sync, | ldf.iPbalancing | 0
| Reference Busbar (NetElements\Substation\Terminal) | ldf.rembar
| Angle | ldf.phiini | 0
Advanced Options | Load Flow Method ( NR Current, 1 NR (Power Eqn Classic) | ldf.i_power | 1
| No Topology Rebuild | ldf.iopt_notopo | 1
| No initialisation | ldf.iopt_noinit | 0
| Consideration of transformer winding ratio | ldf.utr_init | 1
| Max Transformer Phase Shift | ldf.maxPhaseShift | 20
| Tap Adjustment ( 0 Direct, 1 Step) | ldf.itapopt | 0
| Min COntroller Relaxation Factor | ldf.krelax | 1
| Station Controller (0 Standard, 1 Gen HV, 2 Gen LV | ldf.iopt_stamode | 0
| Modelling Method of Towers (0 With In/ Output signals, 1 ignore couplings, 2 equation in lines) | ldf.iopt_igntow | 2
| Use this load flow for initialisation of OPF | ldf.initOPF | 0
| Zone Scaling ( 0 Consider all loads, 1 Consider adjustable loads only) | ldf.zoneScale | 1
Iteration Control | Max No Iterations for Newton-Raphson Iteration | ldf.itrlx | 25
| Max No Iterations for Outer Loop | ldf.ictrlx | 20
| Max No Iterations for Number of steps | ldf.nsteps | 1
| Max Acceptable Load Flow Error for Nodes | ldf.errlf | 1
| Max Acceptable Load Flow Error for Model Equations | ldf.erreq | 0.1
| Iteration Step Size ( 0 Automatic, 1 Fixed Relaxation) | ldf.iStepAdapt | 0
| If Fixed Relaxation factor | ldf.relax | 1
| Automatic Model Adaption for Convergence | ldf.iopt_lev | 0
Outputs | Show 'outer Loop' Messages | ldf.iShowOutLoopMsg | 1
| Show Convergence Progress Report | ldf.iopt_show | 1
| Number of reported buses/models per iteration | ldf.num_conv | 1
| Show verification report | ldf.iopt_check | 0
| Max Loading of Edge Element | ldf.loadmax | 80
| Lower Limit of Allowed Voltage | ldf.vlmin | 0.95
| Upper Limit of Allowed Voltage | ldf.vlmax | 1.05
| Check Control Conditions | ldf.iopt_chctr | 1
Load Generation Scaling | Load Scaling Factor | ldf.scLoadFac | 100
| Generation Scaling Factor | ldf.scGenFac | 100
| Motor Scaling Factor | ldf.scMotFac | 100
Low Voltage Analysis | Fixed Load kVA | ldf.Sfix | 0
| Power Factor of Fixed Load | ldf.cosfix | 0.9
| Max Power Per Customer kVA | ldf.Svar | 12
| Power Factor of Variable Part | ldf.cosvar | 0.95
| Coincidence Factor | ldf.ginf | 0.1
| Voltage Drop Analysis (0 Stochastic Evaluation, 1 Maximum Current Estimation) | ldf.i_volt | 0
Advanced Simulation Optns | Consider Protection Devices ( 0 None, 1 all, 2 Main, 3 Backup) | ldf.iopt_prot | 1
| Ignore Composite Elements | ldf.ign_comp | 0
Note on D4: Author: Either enter the name of the Load Flow command in the study case (typically "Load Flow Calculation.ComLdf") to use or set to False and populate the settings below.

## Frequency_Sweep
Frequency Sweep Settings
Study Case Frequency Sweep | Name of frequency scan settings to be used for studycase (enter FALSE to use settings below) | ComFsweep | FALSE
Basic | Nominal Frequency | frq.fnom | 50
| Network Representation (0=Balanced 1=Unbalanced) | frq.iopt_net | 0
| Impedance Calculation Start frequency | frq.fstart | 90
| Stop Frequency | frq.fstop | 2010
| Step Size | frq.fstep | 5
| Automatic Step Size Adaption | frq.i_adapt | 0
Advanced | Setting for Step Size Adaption Maximum Prediction Error | frq.errmax | 0.01
| Minimum Prediction Error | frq.errinc | 0.005
| Step Size Increase Delay | frq.ninc | 10
| Calculate R, X at output frequency for all nodes | frq.ioutall | 0
Note on D4: Author: Either enter the name of the Frequency Sweep command in the study case (typically "Frequency Sweep.ComFsweep") to use or set to False and populate the settings below.
Note on D9: Author: If Include_Convex then recommended to have a value < nominal frequency.

## Loci_Settings
Loci Settings
Settings Applied to All Harmonic Orders |  |  | From Frequency_Sweep worksheet
Harmonic Impedance Polygon Range (+/- Hz) |  | 25 | Nominal Frequency (Hz) |  | 50
Harmonic Impedance Percentage to Exclude (%) |  | 0 | Frequency Scan Start Frequency (Hz) |  | 90
Maximum number of vertices |  | Unlimited | Frequency Scan Stop Frequency (Hz) |  | 2010
Settings Applied to Individual Harmonic Orders
Harmonic Number | Harmonic Frequency (Hz) | Minimum Frequency (Hz) | Maximum Frequency (Hz) | Percentage to Exclude (%) | Maximum No. Vertices
2 | 100 | 75 | 125 | 5 | 10
3 | 150 | 125 | 175 | 5 | 10
4 | 200 | 175 | 225 | 5 | 10
5 | 250 | 225 | 275 | 5 | 10
6 | 300 | 275 | 325 | 5 | 10
7 | 350 | 325 | 375 | 5 | 10
8 | 400 | 375 | 425 | 5 | 10
9 | 450 | 425 | 475 | 5 | 10
10 | 500 | 475 | 525 | 5 | 10
11 | 550 | 525 | 575 | 5 | 10
12 | 600 | 575 | 625 | 5 | 10
13 | 650 | 625 | 675 | 5 | 10
14 | 700 | 675 | 725 | 5 | 10
15 | 750 | 725 | 775 | 5 | 10
16 | 800 | 775 | 825 | 5 | 10
17 | 850 | 825 | 875 | 5 | 10
18 | 900 | 875 | 925 | 5 | 10
19 | 950 | 925 | 975 | 5 | 10
20 | 1000 | 975 | 1025 | 5 | 10
21 | 1050 | 1025 | 1075 | 5 | 10
22 | 1100 | 1075 | 1125 | 5 | 10
23 | 1150 | 1125 | 1175 | 5 | 10
24 | 1200 | 1175 | 1225 | 5 | 10
25 | 1250 | 1225 | 1275 | 5 | 10
26 | 1300 | 1275 | 1325 | 5 | 10
27 | 1350 | 1325 | 1375 | 5 | 10
28 | 1400 | 1375 | 1425 | 5 | 10
29 | 1450 | 1425 | 1475 | 5 | 10
30 | 1500 | 1475 | 1525 | 5 | 10
31 | 1550 | 1525 | 1575 | 5 | 10
32 | 1600 | 1575 | 1625 | 5 | 10
33 | 1650 | 1625 | 1675 | 5 | 10
34 | 1700 | 1675 | 1725 | 5 | 10
35 | 1750 | 1725 | 1775 | 5 | 10
36 | 1800 | 1775 | 1825 | 5 | 10
37 | 1850 | 1825 | 1875 | 5 | 10
38 | 1900 | 1875 | 1925 | 5 | 10
39 | 1950 | 1925 | 1975 | 5 | 10
40 | 2000 | 1975 | 2025 | 5 | 10
41 | 2050 | 2025 | 2075 | 5 | 10
42 | 2100 | 2075 | 2125 | 5 | 10
43 | 2150 | 2125 | 2175 | 5 | 10
44 | 2200 | 2175 | 2225 | 5 | 10
45 | 2250 | 2225 | 2275 | 5 | 10
46 | 2300 | 2275 | 2325 | 5 | 10
47 | 2350 | 2325 | 2375 | 5 | 10
48 | 2400 | 2375 | 2425 | 5 | 10
49 | 2450 | 2425 | 2475 | 5 | 10
50 | 2500 | 2475 | 2525 | 5 | 10
51 | 2550 | 2525 | 2575 | 5 | 10
52 | 2600 | 2575 | 2625 | 5 | 10
53 | 2650 | 2625 | 2675 | 5 | 10
54 | 2700 | 2675 | 2725 | 5 | 10
55 | 2750 | 2725 | 2775 | 5 | 10
56 | 2800 | 2775 | 2825 | 5 | 10
57 | 2850 | 2825 | 2875 | 5 | 10
58 | 2900 | 2875 | 2925 | 5 | 10
59 | 2950 | 2925 | 2975 | 5 | 10
60 | 3000 | 2975 | 3025 | 5 | 10
61 | 3050 | 3025 | 3075 | 5 | 10
62 | 3100 | 3075 | 3125 | 5 | 10
63 | 3150 | 3125 | 3175 | 5 | 10
64 | 3200 | 3175 | 3225 | 5 | 10
65 | 3250 | 3225 | 3275 | 5 | 10
66 | 3300 | 3275 | 3325 | 5 | 10
67 | 3350 | 3325 | 3375 | 5 | 10
68 | 3400 | 3375 | 3425 | 5 | 10
69 | 3450 | 3425 | 3475 | 5 | 10
70 | 3500 | 3475 | 3525 | 5 | 10
71 | 3550 | 3525 | 3575 | 5 | 10
72 | 3600 | 3575 | 3625 | 5 | 10
73 | 3650 | 3625 | 3675 | 5 | 10
74 | 3700 | 3675 | 3725 | 5 | 10
75 | 3750 | 3725 | 3775 | 5 | 10
76 | 3800 | 3775 | 3825 | 5 | 10
77 | 3850 | 3825 | 3875 | 5 | 10
78 | 3900 | 3875 | 3925 | 5 | 10
79 | 3950 | 3925 | 3975 | 5 | 10
80 | 4000 | 3975 | 4025 | 5 | 10
81 | 4050 | 4025 | 4075 | 5 | 10
82 | 4100 | 4075 | 4125 | 5 | 10
83 | 4150 | 4125 | 4175 | 5 | 10
84 | 4200 | 4175 | 4225 | 5 | 10
85 | 4250 | 4225 | 4275 | 5 | 10
86 | 4300 | 4275 | 4325 | 5 | 10
87 | 4350 | 4325 | 4375 | 5 | 10
88 | 4400 | 4375 | 4425 | 5 | 10
89 | 4450 | 4425 | 4475 | 5 | 10
90 | 4500 | 4475 | 4525 | 5 | 10
91 | 4550 | 4525 | 4575 | 5 | 10
92 | 4600 | 4575 | 4625 | 5 | 10
93 | 4650 | 4625 | 4675 | 5 | 10
94 | 4700 | 4675 | 4725 | 5 | 10
95 | 4750 | 4725 | 4775 | 5 | 10
96 | 4800 | 4775 | 4825 | 5 | 10
97 | 4850 | 4825 | 4875 | 5 | 10
98 | 4900 | 4875 | 4925 | 5 | 10
99 | 4950 | 4925 | 4975 | 5 | 10
100 | 5000 | 4975 | 5025 | 5 | 10
Note on C5: Author: If some harmonic impedance values are excluded they may still end up inside the polygon if the number of vertices is not "Unlimited"