## Clonee 220 kV
Terminal | Clonee 220 kV |  | Terminal | Clonee 220 kV
Terminal Name | Clonee 220 kV |  | Terminal Name | Clonee 220 kV_Corduff 110 kV |  | Clonee 220 kV_Corduff 220 kV |  | Clonee 220 kV_Woodland 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.8217 | 12.9573 | 50 | 3.032 | 2.4835 | 7.617 | 5.7105 | 6.5262 | 7.5388
100 | 21.3 | 28.6479 | 100 | 7.8366 | 6.6747 | 19.0876 | 15.1524 | 16.6848 | 18.2328
150 | 45.9859 | 48.9294 | 150 | 20.1429 | 18.6054 | 44.9929 | 40.8809 | 41.2195 | 39.5357
200 | 11.1304 | 23.1227 | 200 | 5.7943 | 6.7402 | 10.9275 | 13.2861 | 10.8285 | 8.1579
250 | 20.2093 | 37.6872 | 250 | 5.5922 | 4.4962 | 17.1959 | 10.4762 | 11.2075 | 12.9283
300 | 55.6697 | 56.5062 | 300 | 15.9965 | 12.1614 | 54.9442 | 39.3694 | 38.8092 | 31.6721
350 | 31.5728 | 48.2084 | 350 | 14.5613 | 5.2659 | 43.4776 | 17.0425 | 22.0156 | 13.1583
400 | 6.4252 | 59.2146 | 400 | 4.9368 | 1.4166 | 13.5707 | 4.6194 | 3.5939 | 17.361
450 | 17.6505 | 72.7467 | 450 | 2.1461 | 2.259 | 4.6027 | 2.0586 | 7.2068 | 25.9482
500 | 32.0726 | 86.2265 | 500 | 8.57 | 6.4571 | 17.971 | 9.4022 | 17.0132 | 34.5381
550 | 53.7973 | 96.7551 | 550 | 20.7659 | 14.9809 | 42.2101 | 24.6595 | 32.267 | 41.5944
600 | 73.365 | 87.5155 | 600 | 29.9328 | 24.7747 | 74.0263 | 48.2842 | 47.4473 | 33.5142
650 | 46.344 | 94.9413 | 650 | 19.9591 | 14.689 | 62.1651 | 26.202 | 29.6501 | 27.1257
700 | 21.5595 | 110.4182 | 700 | 23.5653 | 9.1532 | 48.6061 | 14.7057 | 17.5433 | 37.3713
750 | 5.966 | 116.4284 | 750 | 17.2173 | 6.5168 | 26.6636 | 11.1901 | 7.507 | 38.4229
800 | 11.0226 | 129.7077 | 800 | 13.245 | 6.7824 | 18.5588 | 8.5837 | 2.4632 | 45.4528
850 | 17.5602 | 146.3091 | 850 | 17.3408 | 9.8823 | 12.8206 | 6.6202 | 4.121 | 56.9014
900 | 21.4389 | 148.4237 | 900 | 6.3399 | 6.5829 | 9.8577 | 4.8581 | 5.6343 | 55.9183
950 | 26.0995 | 158.1749 | 950 | 9.1613 | 6.9042 | 6.5498 | 2.8538 | 8.3366 | 58.0619
1000 | 29.9449 | 167.2785 | 1000 | 10.6948 | 9.9867 | 4.2605 | 1.7517 | 10.3633 | 61.4099
1050 | 33.2126 | 170.1171 | 1050 | 3.5067 | 6.2394 | 2.3292 | 1.0551 | 11.634 | 60.5806
1100 | 36.9905 | 187.1904 | 1100 | 0.49869 | 2.5578 | 1.5006 | 0.64112 | 13.8003 | 68.8036
1150 | 40.5069 | 199.6873 | 1150 | 2.9006 | 7.905 | 2.6181 | 1.6508 | 16.6095 | 77.0332
1200 | 43.6344 | 207.6516 | 1200 | 3.7696 | 14.3041 | 4.1124 | 2.1716 | 17.4526 | 77.4513
1250 | 47.553 | 230.2087 | 1250 | 0.87173 | 6.7579 | 5.8924 | 3.632 | 21.002 | 93.0027
1300 | 51.4693 | 254.5594 | 1300 | 0.90143 | 6.6109 | 7.6314 | 5.0781 | 25.1257 | 112.4889
1350 | 54.837 | 270.2781 | 1350 | 3.5612 | 6.4375 | 9.2061 | 5.8891 | 27.1723 | 120.7556
1400 | 56.5252 | 243.8157 | 1400 | 2.682 | 3.5665 | 10.4588 | 5.992 | 27.9803 | 106.6121
1450 | 59.2852 | 256.4163 | 1450 | 2.4747 | 2.3953 | 11.8579 | 5.9658 | 24.8669 | 94.7785
1500 | 64.0564 | 287.0527 | 1500 | 2.2969 | 3.6282 | 13.983 | 8.4667 | 31.2082 | 122.0962
1550 | 68.318 | 311.6755 | 1550 | 2.2307 | 1.9632 | 16.0631 | 10.6816 | 34.2852 | 134.6261
1600 | 73.9491 | 356.6758 | 1600 | 1.5627 | 1.892 | 18.6855 | 14.7426 | 41.6915 | 171.9024
1650 | 78.0335 | 374.0167 | 1650 | 2.6665 | 3.2715 | 20.7455 | 16.8395 | 46.4659 | 189.8088
1700 | 82.4989 | 352.414 | 1700 | 3.4067 | 8.0591 | 23.3215 | 20.024 | 59.1857 | 214.2527
1750 | 76.6831 | 286.4863 | 1750 | 0.97424 | 2.4934 | 21.1831 | 10.1472 | 32.0522 | 99.8842
1800 | 85.2009 | 352.0918 | 1800 | 1.4666 | 2.0748 | 25.2674 | 15.8282 | 42.8152 | 147.6372
1850 | 89.4755 | 361.1717 | 1850 | 0.33163 | 6.5855 | 27.8454 | 18.3608 | 47.2599 | 157.5421
1900 | 95.677 | 404.2261 | 1900 | 2.8083 | 7.1497 | 31.159 | 22.0706 | 52.0409 | 181.121
1950 | 99.0978 | 409.0652 | 1950 | 3.1745 | 4.4061 | 33.2847 | 21.8819 | 52.2535 | 177.2359
2000 | 113.6602 | 544.3404 | 2000 | 1.8441 | 2.985 | 41.3354 | 39.0404 | 74.1108 | 289.4062

## Corduff 110 kV
Terminal | Corduff 110 kV |  | Terminal | Corduff 110 kV
Terminal Name | Corduff 110 kV |  | Terminal Name | Corduff 110 kV_Clonee 220 kV |  | Corduff 110 kV_Corduff 220 kV |  | Corduff 110 kV_Woodland 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 3.5832 | 3.6526 | 50 | 3.032 | 2.4835 | 3.1931 | 3.4411 | 2.6333 | 2.4964
100 | 7.8346 | 8.0136 | 100 | 7.8366 | 6.6747 | 8.1918 | 8.8046 | 7.0041 | 6.7447
150 | 12.9262 | 13.319 | 150 | 20.1429 | 18.6054 | 20.7014 | 22.025 | 19.0039 | 18.8693
200 | 7.1285 | 7.3587 | 200 | 5.7943 | 6.7402 | 5.6501 | 5.7374 | 6.43 | 6.8301
250 | 11.2259 | 11.3211 | 250 | 5.5922 | 4.4962 | 6.1789 | 7.7587 | 4.5204 | 4.5476
300 | 17.3221 | 18.5591 | 300 | 15.9965 | 12.1614 | 17.7878 | 26.5598 | 12.1892 | 12.6577
350 | 14.7637 | 13.4702 | 350 | 14.5613 | 5.2659 | 16.958 | 16.0661 | 9.2742 | 5.4786
400 | 19.5211 | 19.7502 | 400 | 4.9368 | 1.4166 | 5.9169 | 5.3588 | 2.6025 | 1.4687
450 | 26.5831 | 26.5905 | 450 | 2.1461 | 2.259 | 2.1141 | 2.1149 | 2.2466 | 2.2873
500 | 35.286 | 35.4203 | 500 | 8.57 | 6.4571 | 9.1726 | 9.5677 | 7.2206 | 6.5575
550 | 41.4676 | 42.2805 | 550 | 20.7659 | 14.9809 | 22.5451 | 25.2362 | 16.5694 | 15.1905
600 | 32.4675 | 32.0965 | 600 | 29.9328 | 24.7747 | 32.5587 | 43.0113 | 24.6116 | 25.234
650 | 41.1053 | 39.098 | 650 | 19.9591 | 14.689 | 22.349 | 24.8966 | 15.5259 | 14.8139
700 | 38.0423 | 39.2817 | 700 | 23.5653 | 9.1532 | 26.9555 | 23.6183 | 15.2096 | 9.3691
750 | 61.0456 | 61.998 | 750 | 17.2173 | 6.5168 | 19.8164 | 18.5117 | 10.7133 | 6.6997
800 | 75.7111 | 76.0339 | 800 | 13.245 | 6.7824 | 14.7628 | 14.3005 | 9.3982 | 6.8972
850 | 150.8623 | 151.2937 | 850 | 17.3408 | 9.8823 | 19.0238 | 18.7846 | 13.1574 | 10.072
900 | 89.1761 | 89.0551 | 900 | 6.3399 | 6.5829 | 8.2782 | 7.8483 | 3.7737 | 6.6285
950 | 181.3342 | 181.4061 | 950 | 9.1613 | 6.9042 | 9.7596 | 9.7422 | 7.983 | 7.1143
1000 | 339.0074 | 338.8077 | 1000 | 10.6948 | 9.9867 | 11.1766 | 11.1127 | 9.9167 | 10.0925
1050 | 173.4146 | 173.4156 | 1050 | 3.5067 | 6.2394 | 2.9269 | 2.9231 | 5.1769 | 6.228
1100 | 115.0002 | 115.0604 | 1100 | 0.49869 | 2.5578 | 1.1806 | 1.1839 | 1.5282 | 2.6791
1150 | 86.1402 | 85.9603 | 1150 | 2.9006 | 7.905 | 1.7433 | 1.7133 | 5.706 | 7.6458
1200 | 77.8603 | 78.6538 | 1200 | 3.7696 | 14.3041 | 1.955 | 1.9496 | 10.0712 | 13.8153
1250 | 69.0739 | 68.849 | 1250 | 0.87173 | 6.7579 | 1.893 | 1.9715 | 3.9372 | 6.5058
1300 | 55.7858 | 55.6209 | 1300 | 0.90143 | 6.6109 | 2.0178 | 2.1107 | 3.4734 | 6.3854
1350 | 53.3374 | 53.3031 | 1350 | 3.5612 | 6.4375 | 2.9256 | 2.8699 | 4.9661 | 6.2026
1400 | 46.6114 | 46.6402 | 1400 | 2.682 | 3.5665 | 2.6094 | 2.5694 | 3.3528 | 3.4142
1450 | 40.5671 | 40.5694 | 1450 | 2.4747 | 2.3953 | 2.5335 | 2.5333 | 2.2758 | 2.2605
1500 | 36.8069 | 36.8258 | 1500 | 2.2969 | 3.6282 | 2.4193 | 2.4145 | 2.8188 | 3.4205
1550 | 32.9403 | 32.9425 | 1550 | 2.2307 | 1.9632 | 2.368 | 2.3647 | 1.9315 | 1.8831
1600 | 29.8397 | 29.8127 | 1600 | 1.5627 | 1.892 | 2.092 | 2.1305 | 0.48688 | 1.6865
1650 | 28.6905 | 28.7003 | 1650 | 2.6665 | 3.2715 | 2.5352 | 2.4731 | 2.7637 | 2.9836
1700 | 27.0389 | 27.1792 | 1700 | 3.4067 | 8.0591 | 2.6075 | 2.1815 | 6.1825 | 7.4592
1750 | 24.8765 | 24.8214 | 1750 | 0.97424 | 2.4934 | 1.8172 | 1.9978 | 1.4978 | 2.3306
1800 | 23.1519 | 23.1269 | 1800 | 1.4666 | 2.0748 | 1.9695 | 2.0248 | 1.2741 | 1.9338
1850 | 22.098 | 21.9584 | 1850 | 0.33163 | 6.5855 | 1.3123 | 1.6254 | 3.7003 | 6.0222
1900 | 20.4168 | 20.489 | 1900 | 2.8083 | 7.1497 | 2.447 | 2.5138 | 4.3036 | 6.3915
1950 | 19.957 | 19.9563 | 1950 | 3.1745 | 4.4061 | 2.8373 | 2.727 | 3.421 | 3.8527
2000 | 20.1699 | 20.1309 | 2000 | 1.8441 | 2.985 | 2.2689 | 2.2847 | 1.1068 | 2.7707

## Corduff 220 kV
Terminal | Corduff 220 kV |  | Terminal | Corduff 220 kV
Terminal Name | Corduff 220 kV |  | Terminal Name | Corduff 220 kV_Clonee 220 kV |  | Corduff 220 kV_Corduff 110 kV |  | Corduff 220 kV_Woodland 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.1779 | 9.0457 | 50 | 7.617 | 5.7105 | 3.1931 | 3.4411 | 6.2255 | 5.7526
100 | 20.2979 | 22.3997 | 100 | 19.0876 | 15.1524 | 8.1918 | 8.8046 | 16.2037 | 15.3368
150 | 46.6249 | 50.7399 | 150 | 44.9929 | 40.8809 | 20.7014 | 22.025 | 41.5802 | 41.4764
200 | 11.3695 | 13.7506 | 200 | 10.9275 | 13.2861 | 5.6501 | 5.7374 | 11.8879 | 13.4152
250 | 19.9813 | 26.0312 | 250 | 17.1959 | 10.4762 | 6.1789 | 7.7587 | 11.3974 | 10.6412
300 | 61.6077 | 92.5047 | 300 | 54.9442 | 39.3694 | 17.7878 | 26.5598 | 40.3344 | 41.03
350 | 50.5728 | 48.6398 | 350 | 43.4776 | 17.0425 | 16.958 | 16.0661 | 28.1557 | 17.6727
400 | 15.9454 | 14.7795 | 400 | 13.5707 | 4.6194 | 5.9169 | 5.3588 | 7.8033 | 4.7708
450 | 5.2713 | 5.3623 | 450 | 4.6027 | 2.0586 | 2.1141 | 2.1149 | 2.9963 | 2.1259
500 | 20.283 | 21.6706 | 500 | 17.971 | 9.4022 | 9.1726 | 9.5677 | 12.4529 | 9.6679
550 | 47.5319 | 55.1962 | 550 | 42.2101 | 24.6595 | 22.5451 | 25.2362 | 29.676 | 25.2461
600 | 84.1504 | 114.3482 | 600 | 74.0263 | 48.2842 | 32.5587 | 43.0113 | 51.288 | 49.3737
650 | 72.0815 | 72.9748 | 650 | 62.1651 | 26.202 | 22.349 | 24.8966 | 39.0016 | 26.6486
700 | 56.4733 | 48.3701 | 700 | 48.6061 | 14.7057 | 26.9555 | 23.6183 | 29.0121 | 15.1576
750 | 30.3886 | 28.5574 | 750 | 26.6636 | 11.1901 | 19.8164 | 18.5117 | 17.3215 | 11.4266
800 | 20.917 | 20.2195 | 800 | 18.5588 | 8.5837 | 14.7628 | 14.3005 | 12.6009 | 8.7348
850 | 14.2105 | 13.991 | 850 | 12.8206 | 6.6202 | 19.0238 | 18.7846 | 9.2788 | 6.7116
900 | 11.1204 | 11.033 | 900 | 9.8577 | 4.8581 | 8.2782 | 7.8483 | 6.9776 | 4.9052
950 | 7.425 | 7.3504 | 950 | 6.5498 | 2.8538 | 9.7596 | 9.7422 | 4.2676 | 2.8666
1000 | 4.8523 | 4.8231 | 1000 | 4.2605 | 1.7517 | 11.1766 | 11.1127 | 2.7034 | 1.7656
1050 | 2.6357 | 2.6321 | 1050 | 2.3292 | 1.0551 | 2.9269 | 2.9231 | 1.5248 | 1.0591
1100 | 1.6997 | 1.7016 | 1100 | 1.5006 | 0.64112 | 1.1806 | 1.1839 | 0.95431 | 0.63719
1150 | 2.8241 | 2.8284 | 1150 | 2.6181 | 1.6508 | 1.7433 | 1.7133 | 2.0243 | 1.6298
1200 | 4.5457 | 4.5628 | 1200 | 4.1124 | 2.1716 | 1.955 | 1.9496 | 2.8465 | 2.1297
1250 | 6.3562 | 6.3721 | 1250 | 5.8924 | 3.632 | 1.893 | 1.9715 | 4.4463 | 3.5459
1300 | 8.1081 | 8.1176 | 1300 | 7.6314 | 5.0781 | 2.0178 | 2.1107 | 6.0861 | 4.9358
1350 | 9.8122 | 9.8293 | 1350 | 9.2061 | 5.8891 | 2.9256 | 2.8699 | 7.1756 | 5.6975
1400 | 11.4009 | 11.4397 | 1400 | 10.4588 | 5.992 | 2.6094 | 2.5694 | 8.157 | 5.7627
1450 | 13.1243 | 13.236 | 1450 | 11.8579 | 5.9658 | 2.5335 | 2.5333 | 7.8544 | 5.7197
1500 | 14.996 | 15.0289 | 1500 | 13.983 | 8.4667 | 2.4193 | 2.4145 | 10.4919 | 8.0569
1550 | 16.9664 | 16.9576 | 1550 | 16.0631 | 10.6816 | 2.368 | 2.3647 | 12.4314 | 10.1195
1600 | 19.1377 | 19.001 | 1600 | 18.6855 | 14.7426 | 2.092 | 2.1305 | 15.8678 | 13.8484
1650 | 21.0881 | 20.8121 | 1650 | 20.7455 | 16.8395 | 2.5352 | 2.4731 | 18.2507 | 15.7613
1700 | 23.1063 | 22.1369 | 1700 | 23.3215 | 20.024 | 2.6075 | 2.1815 | 24.0311 | 18.5511
1750 | 23.7474 | 24.0814 | 1750 | 21.1831 | 10.1472 | 1.8172 | 1.9978 | 13.6204 | 9.358
1800 | 26.8277 | 26.7317 | 1800 | 25.2674 | 15.8282 | 1.9695 | 2.0248 | 18.7889 | 14.4703
1850 | 29.3181 | 29.0464 | 1850 | 27.8454 | 18.3608 | 1.3123 | 1.6254 | 21.6378 | 16.6893
1900 | 32.2935 | 31.8542 | 1900 | 31.159 | 22.0706 | 2.447 | 2.5138 | 24.4847 | 19.8622
1950 | 34.8158 | 34.4517 | 1950 | 33.2847 | 21.8819 | 2.8373 | 2.727 | 25.0888 | 19.7398
2000 | 40.5148 | 39.3336 | 2000 | 41.3354 | 39.0404 | 2.2689 | 2.2847 | 37.0602 | 34.9026

## Woodland 220 kV
Terminal | Woodland 220 kV |  | Terminal | Woodland 220 kV
Terminal Name | Woodland 220 kV |  | Terminal Name | Woodland 220 kV_Clonee 220 kV |  | Woodland 220 kV_Corduff 110 kV |  | Woodland 220 kV_Corduff 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 7.3678 | 7.613 | 50 | 6.5262 | 7.5388 | 2.6333 | 2.4964 | 6.2255 | 5.7526
100 | 18.1749 | 18.4956 | 100 | 16.6848 | 18.2328 | 7.0041 | 6.7447 | 16.2037 | 15.3368
150 | 41.0549 | 40.1592 | 150 | 41.2195 | 39.5357 | 19.0039 | 18.8693 | 41.5802 | 41.4764
200 | 8.995 | 8.31 | 200 | 10.8285 | 8.1579 | 6.43 | 6.8301 | 11.8879 | 13.4152
250 | 12.8662 | 13.4796 | 250 | 11.2075 | 12.9283 | 4.5204 | 4.5476 | 11.3974 | 10.6412
300 | 36.82 | 32.9411 | 300 | 38.8092 | 31.6721 | 12.1892 | 12.6577 | 40.3344 | 41.03
350 | 9.415 | 13.5935 | 350 | 22.0156 | 13.1583 | 9.2742 | 5.4786 | 28.1557 | 17.6727
400 | 11.4679 | 17.9021 | 400 | 3.5939 | 17.361 | 2.6025 | 1.4687 | 7.8033 | 4.7708
450 | 20.2363 | 26.7642 | 450 | 7.2068 | 25.9482 | 2.2466 | 2.2873 | 2.9963 | 2.1259
500 | 29.7172 | 35.5544 | 500 | 17.0132 | 34.5381 | 7.2206 | 6.5575 | 12.4529 | 9.6679
550 | 40.3773 | 42.6375 | 550 | 32.267 | 41.5944 | 16.5694 | 15.1905 | 29.676 | 25.2461
600 | 40.9949 | 34.3645 | 600 | 47.4473 | 33.5142 | 24.6116 | 25.234 | 51.288 | 49.3737
650 | 16.8421 | 27.7398 | 650 | 29.6501 | 27.1257 | 15.5259 | 14.8139 | 39.0016 | 26.6486
700 | 17.5334 | 38.0859 | 700 | 17.5433 | 37.3713 | 15.2096 | 9.3691 | 29.0121 | 15.1576
750 | 22.3295 | 39.145 | 750 | 7.507 | 38.4229 | 10.7133 | 6.6997 | 17.3215 | 11.4266
800 | 28.0923 | 46.2365 | 800 | 2.4632 | 45.4528 | 9.3982 | 6.8972 | 12.6009 | 8.7348
850 | 35.6059 | 57.6394 | 850 | 4.121 | 56.9014 | 13.1574 | 10.072 | 9.2788 | 6.7116
900 | 37.4583 | 56.3822 | 900 | 5.6343 | 55.9183 | 3.7737 | 6.6285 | 6.9776 | 4.9052
950 | 39.8026 | 58.2994 | 950 | 8.3366 | 58.0619 | 7.983 | 7.1143 | 4.2676 | 2.8666
1000 | 42.7204 | 61.4322 | 1000 | 10.3633 | 61.4099 | 9.9167 | 10.0925 | 2.7034 | 1.7656
1050 | 43.8246 | 60.4335 | 1050 | 11.634 | 60.5806 | 5.1769 | 6.228 | 1.5248 | 1.0591
1100 | 48.3036 | 68.343 | 1100 | 13.8003 | 68.8036 | 1.5282 | 2.6791 | 0.95431 | 0.63719
1150 | 54.1939 | 76.0625 | 1150 | 16.6095 | 77.0332 | 5.706 | 7.6458 | 2.0243 | 1.6298
1200 | 54.3688 | 76.0158 | 1200 | 17.4526 | 77.4513 | 10.0712 | 13.8153 | 2.8465 | 2.1297
1250 | 62.6493 | 90.9371 | 1250 | 21.002 | 93.0027 | 3.9372 | 6.5058 | 4.4463 | 3.5459
1300 | 72.6147 | 109.3583 | 1300 | 25.1257 | 112.4889 | 3.4734 | 6.3854 | 6.0861 | 4.9358
1350 | 76.7086 | 116.8055 | 1350 | 27.1723 | 120.7556 | 4.9661 | 6.2026 | 7.1756 | 5.6975
1400 | 76.6087 | 102.4853 | 1400 | 27.9803 | 106.6121 | 3.3528 | 3.4142 | 8.157 | 5.7627
1450 | 66.4379 | 90.8023 | 1450 | 24.8669 | 94.7785 | 2.2758 | 2.2605 | 7.8544 | 5.7197
1500 | 81.2473 | 116.0931 | 1500 | 31.2082 | 122.0962 | 2.8188 | 3.4205 | 10.4919 | 8.0569
1550 | 86.9444 | 127.715 | 1550 | 34.2852 | 134.6261 | 1.9315 | 1.8831 | 12.4314 | 10.1195
1600 | 103.1079 | 161.6169 | 1600 | 41.6915 | 171.9024 | 0.48688 | 1.6865 | 15.8678 | 13.8484
1650 | 113.1788 | 177.6189 | 1650 | 46.4659 | 189.8088 | 2.7637 | 2.9836 | 18.2507 | 15.7613
1700 | 140.9831 | 198.4785 | 1700 | 59.1857 | 214.2527 | 6.1825 | 7.4592 | 24.0311 | 18.5511
1750 | 74.6565 | 92.1298 | 1750 | 32.0522 | 99.8842 | 1.4978 | 2.3306 | 13.6204 | 9.358
1800 | 97.575 | 134.9997 | 1800 | 42.8152 | 147.6372 | 1.2741 | 1.9338 | 18.7889 | 14.4703
1850 | 105.0297 | 143.1978 | 1850 | 47.2599 | 157.5421 | 3.7003 | 6.0222 | 21.6378 | 16.6893
1900 | 113.2284 | 163.0739 | 1900 | 52.0409 | 181.121 | 4.3036 | 6.3915 | 24.4847 | 19.8622
1950 | 112.7975 | 159.8159 | 1950 | 52.2535 | 177.2359 | 3.421 | 3.8527 | 25.0888 | 19.7398
2000 | 155.1615 | 258.613 | 2000 | 74.1108 | 289.4062 | 1.1068 | 2.7707 | 37.0602 | 34.9026