## Clonee 220 kV
Terminal | Clonee 220 kV | [5 empty] | Terminal | Clonee 220 kV
Terminal Name | Clonee 220 kV | [5 empty] | Terminal Name | Clonee 220 kV_Corduff 110 kV | [5 empty] | Clonee 220 kV_Corduff 220 kV | [5 empty] | Clonee 220 kV_Cruiserath 220 kV |  |  |  | Clonee 220 kV_Woodland 220 kV
Study Case | step0 |  | step1 |  | step2 |  | Study Case | step0 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details | [6 empty] | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | m:Z | m:Z | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz | [6 empty] | Frequency in Hz
50 | 8.8217 | 12.9573 | 8.8266 | 12.9636 | 7.8995 | 12.0373 | 50 | 3.032 | 2.4835 | 3.0414 | 2.4671 | 2.7369 | 2.496 | 7.617 | 5.7105 | 7.6243 | 5.7421 | 6.5243 | 5.5934 | 7.6244 | 5.7421 | 6.5244 | 5.5935 | 6.5262 | 7.5388 | 6.5241 | 7.5443 | 5.9809 | 6.6027
100 | 21.3 | 28.6479 | 21.7338 | 29.011 | 21.0881 | 28.562 | 100 | 7.8366 | 6.6747 | 8.0993 | 6.8588 | 8.1014 | 7.5672 | 19.0876 | 15.1524 | 19.5467 | 15.6809 | 18.5561 | 16.6138 | 19.5475 | 15.6816 | 18.5569 | 16.6144 | 16.6848 | 18.2328 | 17.0807 | 18.6122 | 17.3733 | 18.2833
150 | 45.9859 | 48.9294 | 45.4043 | 46.3335 | 32.2536 | 31.1212 | 150 | 20.1429 | 18.6054 | 20.7129 | 19.1538 | 16.1929 | 15.9375 | 44.9929 | 40.8809 | 45.0454 | 41.9432 | 33.3472 | 33.2181 | 45.0494 | 41.9469 | 33.3502 | 33.2211 | 41.2195 | 39.5357 | 41.4618 | 38.9642 | 32.8234 | 31.0221
200 | 11.1304 | 23.1227 | 10.0271 | 23.6872 | 6.7476 | 21.1874 | 200 | 5.7943 | 6.7402 | 4.9334 | 5.9529 | 3.3909 | 3.9294 | 10.9275 | 13.2861 | 9.092 | 11.3585 | 5.4062 | 6.9394 | 9.0934 | 11.3602 | 5.407 | 6.9405 | 10.8285 | 8.1579 | 8.7799 | 6.7977 | 5.8704 | 4.4763
250 | 20.2093 | 37.6872 | 20.6445 | 38.847 | 16.8858 | 34.3346 | 250 | 5.5922 | 4.4962 | 4.962 | 3.6517 | 3.6081 | 3.0267 | 17.1959 | 10.4762 | 16.8306 | 8.7853 | 11.6803 | 7.4388 | 16.8347 | 8.7875 | 11.6832 | 7.4406 | 11.2075 | 12.9283 | 10.6325 | 13.6815 | 8.3231 | 9.4634
300 | 55.6697 | 56.5062 | 61.5113 | 54.042 | 28.9107 | 38.5311 | 300 | 15.9965 | 12.1614 | 19.5787 | 15.1618 | 8.69 | 7.0419 | 54.9442 | 39.3694 | 62.4744 | 47.0156 | 28.5775 | 21.5879 | 62.4964 | 47.0321 | 28.5876 | 21.5955 | 38.8092 | 31.6721 | 43.9383 | 31.5902 | 20.4562 | 14.5536
350 | 31.5728 | 48.2084 | 28.6617 | 48.5174 | 11.6604 | 41.9186 | 350 | 14.5613 | 5.2659 | 14.8135 | 4.9568 | 6.674 | 4.3238 | 43.4776 | 17.0425 | 40.8176 | 15.4181 | 18.5663 | 12.7755 | 40.8372 | 15.4255 | 18.5752 | 12.7816 | 22.0156 | 13.1583 | 20.0719 | 13.3549 | 11.246 | 5.8943
400 | 6.4252 | 59.2146 | 6.265 | 59.8822 | 11.7801 | 55.4814 | 400 | 4.9368 | 1.4166 | 5.3 | 1.6003 | 1.97 | 1.9199 | 13.5707 | 4.6194 | 13.0903 | 4.5795 | 4.4366 | 2.1445 | 13.0984 | 4.5824 | 4.4394 | 2.1459 | 3.5939 | 17.361 | 3.4143 | 18.0235 | 3.0732 | 13.5247
450 | 17.6505 | 72.7467 | 17.6517 | 72.709 | 22.8065 | 67.6613 | 450 | 2.1461 | 2.259 | 2.5107 | 2.6793 | 5.2534 | 5.4587 | 4.6027 | 2.0586 | 4.6372 | 2.0693 | 9.4022 | 6.6091 | 4.6409 | 2.0709 | 9.4096 | 6.6143 | 7.2068 | 25.9482 | 7.2033 | 25.9174 | 10.5357 | 20.9127
500 | 32.0726 | 86.2265 | 32.6132 | 86.1664 | 37.364 | 76.2654 | 500 | 8.57 | 6.4571 | 10.9333 | 8.267 | 17.9767 | 16.5866 | 17.971 | 9.4022 | 18.7809 | 9.8714 | 29.5765 | 23.1025 | 18.7992 | 9.881 | 29.6053 | 23.125 | 17.0132 | 34.5381 | 17.4175 | 34.5331 | 25.2973 | 28.5709
550 | 53.7973 | 96.7551 | 53.4374 | 94.3085 | 22.7574 | 82.4598 | 550 | 20.7659 | 14.9809 | 25.9528 | 18.9978 | 5.2942 | 9.2333 | 42.2101 | 24.6595 | 43.3773 | 25.9962 | 5.8555 | 3.9413 | 43.4283 | 26.0268 | 5.8624 | 3.9459 | 32.267 | 41.5944 | 32.2245 | 39.8771 | 9.0502 | 25.4114
600 | 73.365 | 87.5155 | 60.3753 | 85.3889 | 33.8097 | 90.8711 | 600 | 29.9328 | 24.7747 | 28.1294 | 24.4827 | 7.1016 | 7.3378 | 74.0263 | 48.2842 | 62.0739 | 36.6981 | 16.2437 | 10.8378 | 62.1608 | 36.7495 | 16.2664 | 10.853 | 47.4473 | 33.5142 | 36.2668 | 26.7221 | 16.3956 | 29.0851
650 | 46.344 | 94.9413 | 53.7208 | 99.4489 | 46.0579 | 110.2429 | 650 | 19.9591 | 14.689 | 43.133 | 16.6338 | 11.9755 | 10.0185 | 62.1651 | 26.202 | 77.2562 | 20.005 | 26.9078 | 21.9699 | 77.3832 | 20.0379 | 26.952 | 22.006 | 29.6501 | 27.1257 | 32.6776 | 31.5626 | 28.3551 | 43.5446
700 | 21.5595 | 110.4182 | 12.1161 | 110.989 | 55.6015 | 112.2119 | 700 | 23.5653 | 9.1532 | 27.3324 | 14.1596 | 30.3069 | 24.5588 | 48.6061 | 14.7057 | 35.3071 | 12.9155 | 39.1208 | 31.796 | 35.3743 | 12.9401 | 39.1954 | 31.8566 | 17.5433 | 37.3713 | 12.2413 | 38.6073 | 36.8609 | 45.8951
750 | 5.966 | 116.4284 | 11.7212 | 116.7185 | 56.4205 | 120.9456 | 750 | 17.2173 | 6.5168 | 31.792 | 11.7011 | 57.7888 | 46.7685 | 26.6636 | 11.1901 | 22.3927 | 8.4008 | 40.7294 | 30.679 | 22.4417 | 8.4192 | 40.8185 | 30.7461 | 7.507 | 38.4229 | 6.1356 | 38.2732 | 35.7291 | 45.677
800 | 11.0226 | 129.7077 | 14.5356 | 130.4259 | 72.4953 | 149.2261 | 800 | 13.245 | 6.7824 | 31.3078 | 16.7219 | 95.0158 | 88.1666 | 18.5588 | 8.5837 | 18.0426 | 7.9964 | 59.2276 | 52.9206 | 18.0875 | 8.0163 | 59.3749 | 53.0523 | 2.4632 | 45.4528 | 5.1255 | 46.2332 | 58.5517 | 73.7716
850 | 17.5602 | 146.3091 | 15.8973 | 145.9099 | 93.9842 | 97.9927 | 850 | 17.3408 | 9.8823 | 9.1476 | 5.1815 | 63.646 | 71.1741 | 12.8206 | 6.6202 | 14.7038 | 7.6069 | 108.1099 | 119.2154 | 14.7451 | 7.6282 | 108.4136 | 119.5503 | 4.121 | 56.9014 | 3.1476 | 56.4365 | 113.5175 | 108.2911
900 | 21.4389 | 148.4237 | 21.6261 | 151.0938 | 23.3257 | 87.627 | 900 | 6.3399 | 6.5829 | 6.477 | 8.8958 | 29.6728 | 37.4594 | 9.8577 | 4.8581 | 9.9389 | 3.9834 | 42.0161 | 53.7906 | 9.9702 | 3.9959 | 42.1484 | 53.96 | 5.6343 | 55.9183 | 6.4974 | 58.5052 | 44.9197 | 32.1471
950 | 26.0995 | 158.1749 | 25.8319 | 159.1583 | 10.8235 | 104.3565 | 950 | 9.1613 | 6.9042 | 3.7012 | 3.4606 | 12.8316 | 20.2978 | 6.5498 | 2.8538 | 6.8743 | 2.9651 | 27.2804 | 40.5974 | 6.8984 | 2.9755 | 27.3762 | 40.7399 | 8.3366 | 58.0619 | 8.3209 | 59.2525 | 28.9727 | 12.9065
1000 | 29.9449 | 167.2785 | 29.9 | 167.7 | 15.3195 | 130.375 | 1000 | 10.6948 | 9.9867 | 1.4952 | 1.7581 | 6.3133 | 10.1279 | 4.2605 | 1.7517 | 4.2473 | 1.7757 | 17.3681 | 30.4611 | 4.2638 | 1.7826 | 17.4357 | 30.5796 | 10.3633 | 61.4099 | 10.6045 | 62.5294 | 16.5404 | 26.6282
1050 | 33.2126 | 170.1171 | 33.0906 | 166.4644 | 24.8405 | 147.7275 | 1050 | 3.5067 | 6.2394 | 0.96807 | 2.4997 | 2.2327 | 5.6683 | 2.3292 | 1.0551 | 2.3226 | 1.288 | 11.4643 | 16.1497 | 2.3325 | 1.2935 | 11.5135 | 16.2189 | 11.634 | 60.5806 | 11.3215 | 57.5251 | 6.2373 | 40.166
1100 | 36.9905 | 187.1904 | 36.8008 | 184.9216 | 35.6987 | 183.2004 | 1100 | 0.49869 | 2.5578 | 0.60516 | 2.2397 | 1.9718 | 4.2379 | 1.5006 | 0.64112 | 1.7966 | 1.6484 | 8.4629 | 9.8771 | 1.805 | 1.6562 | 8.5027 | 9.9236 | 13.8003 | 68.8036 | 13.7137 | 67.632 | 14.8422 | 70.0381
1150 | 40.5069 | 199.6873 | 39.9607 | 190.7855 | 51.7878 | 247.3527 | 1150 | 2.9006 | 7.905 | 0.37292 | 0.70924 | 1.7431 | 5.9084 | 2.6181 | 1.6508 | 2.5725 | 1.5058 | 17.4179 | 31.2964 | 2.5857 | 1.5135 | 17.5075 | 31.4575 | 16.6095 | 77.0332 | 15.4077 | 70.1099 | 46.6461 | 162.5081
1200 | 43.6344 | 207.6516 | 43.0594 | 197.5584 | 53.8807 | 142.2136 | 1200 | 3.7696 | 14.3041 | 0.28058 | 1.6094 | 0.24701 | 2.2828 | 4.1124 | 2.1716 | 4.0601 | 1.6723 | 37.1371 | 50.0163 | 4.0829 | 1.6816 | 37.3453 | 50.2968 | 17.4526 | 77.4513 | 15.5295 | 67.0002 | 70.3693 | 112.8922
1250 | 47.553 | 230.2087 | 47.3073 | 224.2395 | 19.165 | 99.2791 | 1250 | 0.87173 | 6.7579 | 0.052411 | 0.85733 | 0.18162 | 1.1404 | 5.8924 | 3.632 | 5.9546 | 3.1153 | 30.6727 | 54.8335 | 5.9909 | 3.1343 | 30.8594 | 55.1672 | 21.002 | 93.0027 | 19.9366 | 86.9091 | 54.9449 | 66.943
1300 | 51.4693 | 254.5594 | 51.4474 | 248.6965 | 21.9958 | 124.4204 | 1300 | 0.90143 | 6.6109 | 0.41583 | 1.8331 | 0.9493 | 0.65916 | 7.6314 | 5.0781 | 7.9031 | 4.7507 | 17.4578 | 40.9128 | 7.9552 | 4.782 | 17.5728 | 41.1822 | 25.1257 | 112.4889 | 24.2745 | 106.2261 | 37.5455 | 55.1547
1350 | 54.837 | 270.2781 | 55.3854 | 266.8334 | 21.7197 | 108.5653 | 1350 | 3.5612 | 6.4375 | 1.4183 | 2.7721 | 2.0318 | 3.8515 | 9.2061 | 5.8891 | 9.9189 | 6.4341 | 15.5041 | 38.9336 | 9.9894 | 6.4798 | 15.6142 | 39.2102 | 27.1723 | 120.7556 | 27.2713 | 116.9823 | 42.1399 | 58.2809
1400 | 56.5252 | 243.8157 | 57.7113 | 252.0139 | 25.2545 | 120.777 | 1400 | 2.682 | 3.5665 | 3.3881 | 3.8091 | 3.8846 | 9.791 | 10.4588 | 5.992 | 11.559 | 7.0499 | 11.8381 | 37.5543 | 11.6473 | 7.1038 | 11.9286 | 37.8414 | 27.9803 | 106.6121 | 28.9271 | 111.0417 | 35.6396 | 37.6875
1450 | 59.2852 | 256.4163 | 60.1206 | 255.1649 | 30.4675 | 135.8238 | 1450 | 2.4747 | 2.3953 | 5.4541 | 2.4572 | 3.64 | 17.2692 | 11.8579 | 5.9658 | 12.8826 | 6.6983 | 7.4434 | 36.2996 | 12.9883 | 6.7533 | 7.5045 | 36.5973 | 24.8669 | 94.7785 | 25.3408 | 93.365 | 30.6671 | 26.2681
1500 | 64.0564 | 287.0527 | 64.9335 | 284.5686 | 35.4092 | 151.664 | 1500 | 2.2969 | 3.6282 | 5.3288 | 10.3139 | 2.7312 | 8.789 | 13.983 | 8.4667 | 15.2127 | 9.3161 | 6.3396 | 36.6801 | 15.3463 | 9.3979 | 6.3952 | 37.0023 | 31.2082 | 122.0962 | 31.0473 | 117.082 | 27.2435 | 15.5486
1550 | 68.318 | 311.6755 | 70.0856 | 316.2186 | 38.774 | 167.3478 | 1550 | 2.2307 | 1.9632 | 5.3891 | 11.259 | 2.1497 | 5.4979 | 16.0631 | 10.6816 | 17.9301 | 11.9814 | 3.8302 | 40.2403 | 18.0983 | 12.0938 | 3.8662 | 40.6178 | 34.2852 | 134.6261 | 35.9725 | 138.6896 | 25.6288 | 7.2668
1600 | 73.9491 | 356.6758 | 74.7106 | 349.9396 | 41.4223 | 182.4268 | 1600 | 1.5627 | 1.892 | 10.2912 | 22.0567 | 5.2292 | 11.7745 | 18.6855 | 14.7426 | 20.101 | 14.051 | 4.2132 | 44.4359 | 20.3021 | 14.1916 | 4.2553 | 44.8804 | 41.6915 | 171.9024 | 41.0401 | 164.8635 | 24.8796 | 7.2646
1650 | 78.0335 | 374.0167 | 80.698 | 377.0247 | 43.9122 | 200.0196 | 1650 | 2.6665 | 3.2715 | 6.5985 | 13.4495 | 1.4081 | 8.2294 | 20.7455 | 16.8395 | 23.5802 | 18.739 | 5.804 | 49.6246 | 23.8312 | 18.9384 | 5.8658 | 50.1528 | 46.4659 | 189.8088 | 48.8492 | 192.9853 | 23.9984 | 16.3631
1700 | 82.4989 | 352.414 | 81.0936 | 312.9637 | 49.9445 | 218.6656 | 1700 | 3.4067 | 8.0591 | 4.2737 | 13.2661 | 0.59451 | 7.9508 | 23.3215 | 20.024 | 24.9818 | 17.8218 | 11.7131 | 62.8206 | 25.2642 | 18.0233 | 11.8456 | 63.5309 | 59.1857 | 214.2527 | 51.661 | 166.5827 | 24.7005 | 34.7334
1750 | 76.6831 | 286.4863 | 80.4864 | 293.8402 | 45.946 | 219.1997 | 1750 | 0.97424 | 2.4934 | 1.9984 | 1.005 | 0.44916 | 5.7321 | 21.1831 | 10.1472 | 25.2731 | 11.7805 | 8.1853 | 40.8747 | 25.5761 | 11.9218 | 8.2834 | 41.3647 | 32.0522 | 99.8842 | 34.3499 | 103.9442 | 18.1709 | 30.3561
1800 | 85.2009 | 352.0918 | 91.2169 | 368.503 | 51.608 | 221.2021 | 1800 | 1.4666 | 2.0748 | 3.3692 | 0.58434 | 0.43619 | 6.1945 | 25.2674 | 15.8282 | 31.1907 | 19.6819 | 5.9261 | 46.0824 | 31.5866 | 19.9316 | 6.0013 | 46.6672 | 42.8152 | 147.6372 | 47.1409 | 156.2821 | 20.5754 | 29.4291
1850 | 89.4755 | 361.1717 | 97.4675 | 382.1209 | 53.5344 | 233.265 | 1850 | 0.33163 | 6.5855 | 2.8982 | 3.0305 | 2.1844 | 8.2468 | 27.8454 | 18.3608 | 35.6459 | 24.2788 | 8.0998 | 46.3966 | 36.1241 | 24.6045 | 8.2084 | 47.019 | 47.2599 | 157.5421 | 54.7951 | 174.2509 | 19.6897 | 28.2501
1900 | 95.677 | 404.2261 | 106.6863 | 435.2165 | 57.7818 | 261.8123 | 1900 | 2.8083 | 7.1497 | 4.1803 | 1.9721 | 1.6168 | 8.3349 | 31.159 | 22.0706 | 41.6278 | 30.9113 | 8.884 | 65.7446 | 42.2173 | 31.349 | 9.0098 | 66.6756 | 52.0409 | 181.121 | 62.0148 | 203.6142 | 21.9715 | 45.9898
1950 | 99.0978 | 409.0652 | 121.7725 | 507.2347 | 63.9587 | 286.9114 | 1950 | 3.1745 | 4.4061 | 4.0525 | 2.1035 | 2.3026 | 10.5816 | 33.2847 | 21.8819 | 52.0673 | 48.8608 | 17.6998 | 99.0754 | 52.8445 | 49.5902 | 17.964 | 100.5543 | 52.2535 | 177.2359 | 88.2102 | 294.0686 | 26.3145 | 77.8255
2000 | 113.6602 | 544.3404 | 123.9607 | 469.6391 | 57.7611 | 246.0339 | 2000 | 1.8441 | 2.985 | 3.4458 | 2.1431 | 2.0426 | 3.3608 | 41.3354 | 39.0404 | 55.4246 | 43.6074 | 16.9915 | 42.0373 | 56.2955 | 44.2926 | 17.2585 | 42.6979 | 74.1108 | 289.4062 | 77.9914 | 232.129 | 17.2993 | 36.2789

## Corduff 110 kV
Terminal | Corduff 110 kV | [5 empty] | Terminal | Corduff 110 kV
Terminal Name | Corduff 110 kV | [5 empty] | Terminal Name | Corduff 110 kV_Clonee 220 kV | [5 empty] | Corduff 110 kV_Corduff 220 kV | [5 empty] | Corduff 110 kV_Cruiserath 220 kV |  |  |  | Corduff 110 kV_Woodland 220 kV
Study Case | step0 |  | step1 |  | step2 |  | Study Case | step0 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details | [6 empty] | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | m:Z | m:Z | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz | [6 empty] | Frequency in Hz
50 | 3.5832 | 3.6526 | 3.5961 | 3.6374 | 3.4854 | 3.4994 | 50 | 3.032 | 2.4835 | 3.0414 | 2.4671 | 2.7369 | 2.496 | 3.1931 | 3.4411 | 3.2038 | 3.4224 | 2.8183 | 2.8719 | 3.2038 | 3.4224 | 2.8182 | 2.8718 | 2.6333 | 2.4964 | 2.6391 | 2.4797 | 2.5462 | 2.5098
100 | 7.8346 | 8.0136 | 7.9973 | 8.1108 | 8.0138 | 8.0539 | 100 | 7.8366 | 6.6747 | 8.0993 | 6.8588 | 8.1014 | 7.5672 | 8.1918 | 8.8046 | 8.4644 | 9.0342 | 8.2875 | 8.4244 | 8.4653 | 9.0353 | 8.2883 | 8.4253 | 7.0041 | 6.7447 | 7.2425 | 6.9292 | 7.7179 | 7.6476
150 | 12.9262 | 13.319 | 12.4602 | 12.6284 | 7.8208 | 7.8864 | 150 | 20.1429 | 18.6054 | 20.7129 | 19.1538 | 16.1929 | 15.9375 | 20.7014 | 22.025 | 21.2458 | 22.4264 | 16.3128 | 16.4786 | 21.252 | 22.434 | 16.3167 | 16.4827 | 19.0039 | 18.8693 | 19.6401 | 19.4162 | 16.1224 | 16.1556
200 | 7.1285 | 7.3587 | 7.4312 | 7.6581 | 7.792 | 7.8337 | 200 | 5.7943 | 6.7402 | 4.9334 | 5.9529 | 3.3909 | 3.9294 | 5.6501 | 5.7374 | 4.772 | 4.8297 | 3.2436 | 3.1754 | 4.7792 | 4.8399 | 3.2467 | 3.1788 | 6.43 | 6.8301 | 5.6266 | 6.0237 | 3.8566 | 3.9674
250 | 11.2259 | 11.3211 | 11.929 | 12.0982 | 12.2097 | 12.3014 | 250 | 5.5922 | 4.4962 | 4.962 | 3.6517 | 3.6081 | 3.0267 | 6.1789 | 7.7587 | 5.6064 | 7.178 | 3.923 | 4.2878 | 5.6159 | 7.1882 | 3.9302 | 4.2952 | 4.5204 | 4.5476 | 3.7729 | 3.6933 | 3.1156 | 3.1142
300 | 17.3221 | 18.5591 | 18.4703 | 18.985 | 14.9516 | 14.8257 | 300 | 15.9965 | 12.1614 | 19.5787 | 15.1618 | 8.69 | 7.0419 | 17.7878 | 26.5598 | 21.69 | 32.1725 | 9.4323 | 10.5312 | 21.6985 | 32.1823 | 9.4381 | 10.5365 | 12.1892 | 12.6577 | 15.0654 | 15.7701 | 7.2416 | 7.3249
350 | 14.7637 | 13.4702 | 15.5012 | 14.5901 | 17.3627 | 17.3368 | 350 | 14.5613 | 5.2659 | 14.8135 | 4.9568 | 6.674 | 4.3238 | 16.958 | 16.0661 | 17.3151 | 15.7045 | 7.3602 | 7.2875 | 17.3146 | 15.7061 | 7.3434 | 7.2714 | 9.2742 | 5.4786 | 9.2893 | 5.1603 | 5.185 | 4.5057
400 | 19.5211 | 19.7502 | 21.5426 | 21.9422 | 23.4866 | 23.526 | 400 | 4.9368 | 1.4166 | 5.3 | 1.6003 | 1.97 | 1.9199 | 5.9169 | 5.3588 | 6.3368 | 5.6165 | 2.1561 | 2.0884 | 6.3381 | 5.618 | 2.1567 | 2.0892 | 2.6025 | 1.4687 | 2.8622 | 1.6536 | 1.8968 | 1.9606
450 | 26.5831 | 26.5905 | 30.8395 | 30.8648 | 32.3665 | 32.3539 | 450 | 2.1461 | 2.259 | 2.5107 | 2.6793 | 5.2534 | 5.4587 | 2.1141 | 2.1149 | 2.4601 | 2.4244 | 5.2202 | 5.223 | 2.4611 | 2.4254 | 5.2232 | 5.2261 | 2.2466 | 2.2873 | 2.6646 | 2.7121 | 5.5258 | 5.5773
500 | 35.286 | 35.4203 | 43.4853 | 43.5893 | 38.2374 | 38.288 | 500 | 8.57 | 6.4571 | 10.9333 | 8.267 | 17.9767 | 16.5866 | 9.1726 | 9.5677 | 11.6798 | 12.0189 | 18.4293 | 18.7003 | 11.6885 | 12.0282 | 18.4367 | 18.7081 | 7.2206 | 6.5575 | 9.2917 | 8.3973 | 17.2771 | 17.0227
550 | 41.4676 | 42.2805 | 46.9345 | 47.7456 | 47.9431 | 47.634 | 550 | 20.7659 | 14.9809 | 25.9528 | 18.9978 | 5.2942 | 9.2333 | 22.5451 | 25.2362 | 28.0757 | 31.3082 | 4.3241 | 4.2183 | 28.0874 | 31.323 | 4.3312 | 4.2256 | 16.5694 | 15.1905 | 20.9962 | 19.2493 | 8.2037 | 9.2891
600 | 32.4675 | 32.0965 | 40.7452 | 39.1473 | 49.964 | 50.7914 | 600 | 29.9328 | 24.7747 | 28.1294 | 24.4827 | 7.1016 | 7.3378 | 32.5587 | 43.0113 | 30.711 | 41.7256 | 8.2933 | 8.7154 | 30.7734 | 41.8034 | 8.3299 | 8.7511 | 24.6116 | 25.234 | 23.7441 | 24.8673 | 6.9948 | 7.3724
650 | 41.1053 | 39.098 | 30.2008 | 34.4634 | 56.9891 | 57.4483 | 650 | 19.9591 | 14.689 | 43.133 | 16.6338 | 11.9755 | 10.0185 | 22.349 | 24.8966 | 49.3839 | 41.0149 | 12.8664 | 13.0326 | 49.4698 | 41.0854 | 12.8715 | 13.0363 | 15.5259 | 14.8139 | 27.7246 | 17.0294 | 10.6368 | 10.1805
700 | 38.0423 | 39.2817 | 60.8689 | 62.971 | 94.4747 | 95.7669 | 700 | 23.5653 | 9.1532 | 27.3324 | 14.1596 | 30.3069 | 24.5588 | 26.9555 | 23.6183 | 30.6005 | 28.1629 | 32.3029 | 33.229 | 30.6596 | 28.2191 | 32.3448 | 33.275 | 15.2096 | 9.3691 | 19.6417 | 14.3657 | 26.368 | 25.1077
750 | 61.0456 | 61.998 | 126.1047 | 130.6058 | 128.5023 | 129.7071 | 750 | 17.2173 | 6.5168 | 31.792 | 11.7011 | 57.7888 | 46.7685 | 19.8164 | 18.5117 | 36.7168 | 34.1682 | 61.4235 | 63.2772 | 36.8023 | 34.2476 | 61.558 | 63.4162 | 10.7133 | 6.6997 | 19.4819 | 12.0528 | 49.6934 | 47.5174
800 | 75.7111 | 76.0339 | 192.5056 | 194.3153 | 63.3637 | 64.4166 | 800 | 13.245 | 6.7824 | 31.3078 | 16.7219 | 95.0158 | 88.1666 | 14.7628 | 14.3005 | 34.6848 | 33.0763 | 96.6996 | 96.8134 | 34.763 | 33.1517 | 96.9344 | 97.0495 | 9.3982 | 6.8972 | 22.7557 | 16.9941 | 91.6365 | 89.4348
850 | 150.8623 | 151.2937 | 84.2603 | 84.0578 | 91.4021 | 90.4441 | 850 | 17.3408 | 9.8823 | 9.1476 | 5.1815 | 63.646 | 71.1741 | 19.0238 | 18.7846 | 10.046 | 9.6469 | 61.5322 | 61.5409 | 10.0782 | 9.6766 | 61.7283 | 61.7382 | 13.1574 | 10.072 | 6.9752 | 5.2827 | 69.4623 | 71.9911
900 | 89.1761 | 89.0551 | 87.9332 | 87.3313 | 91.971 | 91.8352 | 900 | 6.3399 | 6.5829 | 6.477 | 8.8958 | 29.6728 | 37.4594 | 8.2782 | 7.8483 | 7.4445 | 6.9236 | 27.4322 | 26.662 | 7.4655 | 6.9427 | 27.557 | 26.7861 | 3.7737 | 6.6285 | 6.4509 | 8.9754 | 35.4144 | 37.751
950 | 181.3342 | 181.4061 | 74.5564 | 74.4289 | 76.5192 | 75.9194 | 950 | 9.1613 | 6.9042 | 3.7012 | 3.4606 | 12.8316 | 20.2978 | 9.7596 | 9.7422 | 3.7857 | 3.704 | 10.8221 | 10.0181 | 3.7919 | 3.7125 | 10.8011 | 9.9859 | 7.983 | 7.1143 | 3.7022 | 3.5679 | 18.2262 | 20.475
1000 | 339.0074 | 338.8077 | 48.1732 | 48.1236 | 49.4145 | 49.3232 | 1000 | 10.6948 | 9.9867 | 1.4952 | 1.7581 | 6.3133 | 10.1279 | 11.1766 | 11.1127 | 1.5442 | 1.5004 | 5.3084 | 4.8578 | 1.548 | 1.5036 | 5.3411 | 4.8933 | 9.9167 | 10.0925 | 1.5287 | 1.7381 | 8.886 | 10.1791
1050 | 173.4146 | 173.4156 | 33.3697 | 33.3611 | 33.2538 | 33.1876 | 1050 | 3.5067 | 6.2394 | 0.96807 | 2.4997 | 2.2327 | 5.6683 | 2.9269 | 2.9231 | 0.56367 | 0.55918 | 1.3017 | 1.1284 | 0.56514 | 0.56051 | 1.3347 | 1.1551 | 5.1769 | 6.228 | 1.9713 | 2.4715 | 4.6145 | 5.6866
1100 | 115.0002 | 115.0604 | 26.8668 | 26.8392 | 27.0723 | 27.0103 | 1100 | 0.49869 | 2.5578 | 0.60516 | 2.2397 | 1.9718 | 4.2379 | 1.1806 | 1.1839 | 0.35388 | 0.3503 | 1.6861 | 1.6788 | 0.3702 | 0.36623 | 1.6763 | 1.6718 | 1.5282 | 2.6791 | 1.543 | 2.1417 | 3.2973 | 4.1363
1150 | 86.1402 | 85.9603 | 19.3862 | 19.385 | 19.3822 | 19.4178 | 1150 | 2.9006 | 7.905 | 0.37292 | 0.70924 | 1.7431 | 5.9084 | 1.7433 | 1.7133 | 0.29972 | 0.29122 | 0.83534 | 0.60981 | 0.29564 | 0.28726 | 0.85158 | 0.62247 | 5.706 | 7.6458 | 0.60592 | 0.70786 | 4.025 | 5.8407
1200 | 77.8603 | 78.6538 | 13.9622 | 13.9576 | 13.755 | 13.6996 | 1200 | 3.7696 | 14.3041 | 0.28058 | 1.6094 | 0.24701 | 2.2828 | 1.955 | 1.9496 | 0.27479 | 0.28534 | 0.96778 | 1.554 | 0.27882 | 0.28934 | 0.97006 | 1.562 | 10.0712 | 13.8153 | 1.1229 | 1.5811 | 2.0268 | 2.2473
1250 | 69.0739 | 68.849 | 7.3157 | 7.3137 | 7.2533 | 7.2386 | 1250 | 0.87173 | 6.7579 | 0.052411 | 0.85733 | 0.18162 | 1.1404 | 1.893 | 1.9715 | 0.18816 | 0.19605 | 0.41419 | 0.72539 | 0.18912 | 0.19712 | 0.41918 | 0.73309 | 3.9372 | 6.5058 | 0.51681 | 0.83413 | 1.1003 | 1.1156
1300 | 55.7858 | 55.6209 | 4.9337 | 4.9228 | 4.9607 | 4.9607 | 1300 | 0.90143 | 6.6109 | 0.41583 | 1.8331 | 0.9493 | 0.65916 | 2.0178 | 2.1107 | 0.24283 | 0.24025 | 1.0718 | 1.1689 | 0.24459 | 0.24191 | 1.0809 | 1.1782 | 3.4734 | 6.3854 | 1.169 | 1.7761 | 0.60009 | 0.64446
1350 | 53.3374 | 53.3031 | 17.8022 | 17.8081 | 17.5855 | 17.6329 | 1350 | 3.5612 | 6.4375 | 1.4183 | 2.7721 | 2.0318 | 3.8515 | 2.9256 | 2.8699 | 1.1176 | 1.0732 | 1.325 | 0.95801 | 1.125 | 1.0803 | 1.3307 | 0.95928 | 4.9661 | 6.2026 | 2.1103 | 2.68 | 3.8718 | 3.7271
1400 | 46.6114 | 46.6402 | 51.221 | 51.2008 | 49.7909 | 50.1655 | 1400 | 2.682 | 3.5665 | 3.3881 | 3.8091 | 3.8846 | 9.791 | 2.6094 | 2.5694 | 3.274 | 3.1676 | 2.2044 | 2.335 | 3.2991 | 3.1924 | 2.2367 | 2.372 | 3.3528 | 3.4142 | 3.7649 | 3.7 | 9.4002 | 9.4386
1450 | 40.5671 | 40.5694 | 99.6518 | 99.5066 | 98.5528 | 97.8233 | 1450 | 2.4747 | 2.3953 | 5.4541 | 2.4572 | 3.64 | 17.2692 | 2.5335 | 2.5333 | 6.7143 | 6.7291 | 2.8995 | 6.5408 | 6.771 | 6.7856 | 2.935 | 6.6058 | 2.2758 | 2.2605 | 2.2424 | 2.2984 | 15.6718 | 16.5278
1500 | 36.8069 | 36.8258 | 57.5459 | 57.7235 | 56.1951 | 55.5939 | 1500 | 2.2969 | 3.6282 | 5.3288 | 10.3139 | 2.7312 | 8.789 | 2.4193 | 2.4145 | 4.5867 | 4.4506 | 3.8876 | 6.0046 | 4.642 | 4.5018 | 3.9291 | 6.0425 | 2.8188 | 3.4205 | 7.459 | 9.6687 | 7.5531 | 8.3465
1550 | 32.9403 | 32.9425 | 35.9874 | 35.9376 | 34.828 | 34.6583 | 1550 | 2.2307 | 1.9632 | 5.3891 | 11.259 | 2.1497 | 5.4979 | 2.368 | 2.3647 | 4.0695 | 3.8303 | 2.4544 | 3.5642 | 4.1008 | 3.8592 | 2.4456 | 3.5703 | 1.9315 | 1.8831 | 7.9283 | 10.3295 | 4.867 | 5.5166
1600 | 29.8397 | 29.8127 | 62.7662 | 62.359 | 75.8138 | 75.3413 | 1600 | 1.5627 | 1.892 | 10.2912 | 22.0567 | 5.2292 | 11.7745 | 2.092 | 2.1305 | 7.8251 | 7.3286 | 4.268 | 4.9954 | 7.8931 | 7.3933 | 4.3076 | 5.0689 | 0.48688 | 1.6865 | 15.0332 | 20.1092 | 10.1964 | 11.6367
1650 | 28.6905 | 28.7003 | 48.6083 | 48.8825 | 46.3656 | 46.1555 | 1650 | 2.6665 | 3.2715 | 6.5985 | 13.4495 | 1.4081 | 8.2294 | 2.5352 | 2.4731 | 5.4504 | 5.0276 | 1.2432 | 3.045 | 5.4985 | 5.0783 | 1.2312 | 3.0997 | 2.7637 | 2.9836 | 9.4382 | 12.2668 | 6.1583 | 7.909
1700 | 27.0389 | 27.1792 | 32.8419 | 32.9883 | 31.3419 | 30.9384 | 1700 | 3.4067 | 8.0591 | 4.2737 | 13.2661 | 0.59451 | 7.9508 | 2.6075 | 2.1815 | 2.8771 | 2.3 | 2.7371 | 6.1121 | 2.9423 | 2.3461 | 2.6609 | 6.0183 | 6.1825 | 7.4592 | 9.8042 | 12.1867 | 5.0132 | 7.4882
1750 | 24.8765 | 24.8214 | 29.0261 | 29.0179 | 29.1939 | 28.9999 | 1750 | 0.97424 | 2.4934 | 1.9984 | 1.005 | 0.44916 | 5.7321 | 1.8172 | 1.9978 | 2.5948 | 2.6707 | 1.5126 | 2.7985 | 2.5668 | 2.6609 | 1.7216 | 3.0713 | 1.4978 | 2.3306 | 0.87835 | 0.81693 | 4.054 | 5.2137
1800 | 23.1519 | 23.1269 | 37.6533 | 37.6325 | 37.7202 | 37.494 | 1800 | 1.4666 | 2.0748 | 3.3692 | 0.58434 | 0.43619 | 6.1945 | 1.9695 | 2.0248 | 4.0766 | 4.079 | 2.0545 | 3.8995 | 4.1285 | 4.1369 | 2.0748 | 3.9299 | 1.2741 | 1.9338 | 1.2562 | 0.51809 | 4.411 | 5.6881
1850 | 22.098 | 21.9584 | 34.7774 | 34.7377 | 32.4739 | 31.9044 | 1850 | 0.33163 | 6.5855 | 2.8982 | 3.0305 | 2.1844 | 8.2468 | 1.3123 | 1.6254 | 3.8465 | 3.8895 | 5.0056 | 7.5294 | 3.9369 | 3.9552 | 4.9525 | 7.4643 | 3.7003 | 6.0222 | 1.6942 | 2.6965 | 5.2483 | 7.5188
1900 | 20.4168 | 20.489 | 32.5459 | 32.5543 | 32.5237 | 32.1603 | 1900 | 2.8083 | 7.1497 | 4.1803 | 1.9721 | 1.6168 | 8.3349 | 2.447 | 2.5138 | 4.6275 | 4.5602 | 3.9489 | 7.4043 | 4.6933 | 4.6258 | 4.0783 | 7.6249 | 4.3036 | 6.3915 | 2.4847 | 1.8066 | 4.6866 | 7.5184
1950 | 19.957 | 19.9563 | 25.9351 | 25.9573 | 25.7143 | 25.4682 | 1950 | 3.1745 | 4.4061 | 4.0525 | 2.1035 | 2.3026 | 10.5816 | 2.8373 | 2.727 | 4.2156 | 3.9795 | 5.0268 | 10.7073 | 4.2898 | 4.0452 | 5.046 | 10.763 | 3.421 | 3.8527 | 3.1582 | 1.8674 | 4.9505 | 9.4754
2000 | 20.1699 | 20.1309 | 20.6422 | 20.6569 | 21.0373 | 21.1795 | 2000 | 1.8441 | 2.985 | 3.4458 | 2.1431 | 2.0426 | 3.3608 | 2.2689 | 2.2847 | 3.6731 | 3.5998 | 3.6057 | 4.361 | 3.7043 | 3.6315 | 3.5929 | 4.3564 | 1.1068 | 2.7707 | 2.2833 | 1.8853 | 2.5301 | 2.9862

## Corduff 220 kV
Terminal | Corduff 220 kV | [5 empty] | Terminal | Corduff 220 kV
Terminal Name | Corduff 220 kV | [5 empty] | Terminal Name | Corduff 220 kV_Clonee 220 kV | [5 empty] | Corduff 220 kV_Corduff 110 kV | [5 empty] | Corduff 220 kV_Cruiserath 220 kV |  |  |  | Corduff 220 kV_Woodland 220 kV
Study Case | step0 |  | step1 |  | step2 |  | Study Case | step0 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details | [6 empty] | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | m:Z | m:Z | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz | [6 empty] | Frequency in Hz
50 | 8.1779 | 9.0457 | 8.1879 | 9.1213 | 6.838 | 7.0452 | 50 | 7.617 | 5.7105 | 7.6243 | 5.7421 | 6.5243 | 5.5934 | 3.1931 | 3.4411 | 3.2038 | 3.4224 | 2.8183 | 2.8719 | 8.188 | 9.1214 | 6.8381 | 7.0453 | 6.2255 | 5.7526 | 6.2256 | 5.7842 | 5.7758 | 5.6356
100 | 20.2979 | 22.3997 | 20.7749 | 23.1176 | 19.234 | 19.7417 | 100 | 19.0876 | 15.1524 | 19.5467 | 15.6809 | 18.5561 | 16.6138 | 8.1918 | 8.8046 | 8.4644 | 9.0342 | 8.2875 | 8.4244 | 20.7757 | 23.1185 | 19.2348 | 19.7425 | 16.2037 | 15.3368 | 16.6189 | 15.868 | 17.0637 | 16.8127
150 | 46.6249 | 50.7399 | 46.5068 | 50.8591 | 33.5392 | 33.9887 | 150 | 44.9929 | 40.8809 | 45.0454 | 41.9432 | 33.3472 | 33.2181 | 20.7014 | 22.025 | 21.2458 | 22.4264 | 16.3128 | 16.4786 | 46.5109 | 50.8636 | 33.5422 | 33.9917 | 41.5802 | 41.4764 | 42.0681 | 42.5256 | 33.406 | 33.6592
200 | 11.3695 | 13.7506 | 9.7838 | 12.5691 | 5.4382 | 5.7389 | 200 | 10.9275 | 13.2861 | 9.092 | 11.3585 | 5.4062 | 6.9394 | 5.6501 | 5.7374 | 4.772 | 4.8297 | 3.2436 | 3.1754 | 9.7853 | 12.571 | 5.439 | 5.7398 | 11.8879 | 13.4152 | 9.794 | 11.4397 | 6.5203 | 6.9616
250 | 19.9813 | 26.0312 | 19.8242 | 26.4901 | 13.4543 | 15.2052 | 250 | 17.1959 | 10.4762 | 16.8306 | 8.7853 | 11.6803 | 7.4388 | 6.1789 | 7.7587 | 5.6064 | 7.178 | 3.923 | 4.2878 | 19.829 | 26.4966 | 13.4576 | 15.2089 | 11.3974 | 10.6412 | 10.3204 | 8.9904 | 8.0765 | 7.7603
300 | 61.6077 | 92.5047 | 69.7972 | 106.7068 | 31.6508 | 35.8447 | 300 | 54.9442 | 39.3694 | 62.4744 | 47.0156 | 28.5775 | 21.5879 | 17.7878 | 26.5598 | 21.69 | 32.1725 | 9.4323 | 10.5312 | 69.8217 | 106.7443 | 31.6619 | 35.8573 | 40.3344 | 41.03 | 46.4341 | 48.9493 | 22.2788 | 22.4748
350 | 50.5728 | 48.6398 | 47.6197 | 44.8311 | 20.4244 | 20.5222 | 350 | 43.4776 | 17.0425 | 40.8176 | 15.4181 | 18.5663 | 12.7755 | 16.958 | 16.0661 | 17.3151 | 15.7045 | 7.3602 | 7.2875 | 47.6424 | 44.8525 | 20.4342 | 20.532 | 28.1557 | 17.6727 | 26.1596 | 15.9845 | 14.709 | 13.2639
400 | 15.9454 | 14.7795 | 15.3164 | 14.1911 | 5.1451 | 5.1042 | 400 | 13.5707 | 4.6194 | 13.0903 | 4.5795 | 4.4366 | 2.1445 | 5.9169 | 5.3588 | 6.3368 | 5.6165 | 2.1561 | 2.0884 | 15.326 | 14.2 | 5.1483 | 5.1074 | 7.8033 | 4.7708 | 7.689 | 4.7283 | 2.8158 | 2.2289
450 | 5.2713 | 5.3623 | 5.3139 | 5.4252 | 10.2539 | 10.4334 | 450 | 4.6027 | 2.0586 | 4.6372 | 2.0693 | 9.4022 | 6.6091 | 2.1141 | 2.1149 | 2.4601 | 2.4244 | 5.2202 | 5.223 | 5.3181 | 5.4295 | 10.262 | 10.4416 | 2.9963 | 2.1259 | 3.0131 | 2.1379 | 7.4754 | 6.8112
500 | 20.283 | 21.6706 | 21.2036 | 22.8274 | 31.752 | 32.9517 | 500 | 17.971 | 9.4022 | 18.7809 | 9.8714 | 29.5765 | 23.1025 | 9.1726 | 9.5677 | 11.6798 | 12.0189 | 18.4293 | 18.7003 | 21.2242 | 22.8497 | 31.7829 | 32.9837 | 12.4529 | 9.6679 | 13.0178 | 10.1496 | 24.953 | 23.7739
550 | 47.5319 | 55.1962 | 48.9411 | 58.3183 | 6.4198 | 6.4939 | 550 | 42.2101 | 24.6595 | 43.3773 | 25.9962 | 5.8555 | 3.9413 | 22.5451 | 25.2362 | 28.0757 | 31.3082 | 4.3241 | 4.2183 | 48.9987 | 58.387 | 6.4274 | 6.5016 | 29.676 | 25.2461 | 30.4626 | 26.6319 | 4.5681 | 4.0278
600 | 84.1504 | 114.3482 | 71.9087 | 99.3511 | 17.9214 | 18.4232 | 600 | 74.0263 | 48.2842 | 62.0739 | 36.6981 | 16.2437 | 10.8378 | 32.5587 | 43.0113 | 30.711 | 41.7256 | 8.2933 | 8.7154 | 72.0094 | 99.4902 | 17.9465 | 18.449 | 51.288 | 49.3737 | 40.4795 | 37.5216 | 12.465 | 11.1827
650 | 72.0815 | 72.9748 | 90.7874 | 73.6082 | 28.3403 | 28.592 | 650 | 62.1651 | 26.202 | 77.2562 | 20.005 | 26.9078 | 21.9699 | 22.349 | 24.8966 | 49.3839 | 41.0149 | 12.8664 | 13.0326 | 90.9366 | 73.7291 | 28.3869 | 28.639 | 39.0016 | 26.6486 | 43.7025 | 20.6662 | 23.7443 | 22.4265
700 | 56.4733 | 48.3701 | 40.553 | 36.9631 | 41.6383 | 42.7963 | 700 | 48.6061 | 14.7057 | 35.3071 | 12.9155 | 39.1208 | 31.796 | 26.9555 | 23.6183 | 30.6005 | 28.1629 | 32.3029 | 33.229 | 40.6303 | 37.0336 | 41.7176 | 42.8779 | 29.0121 | 15.1576 | 22.2391 | 13.2402 | 34.0605 | 32.4496
750 | 30.3886 | 28.5574 | 25.8696 | 24.6302 | 43.8116 | 45.0767 | 750 | 26.6636 | 11.1901 | 22.3927 | 8.4008 | 40.7294 | 30.679 | 19.8164 | 18.5117 | 36.7168 | 34.1682 | 61.4235 | 63.2772 | 25.9262 | 24.684 | 43.9074 | 45.1753 | 17.3215 | 11.4266 | 13.6927 | 8.6075 | 33.451 | 31.2265
800 | 20.917 | 20.2195 | 20.4293 | 19.8328 | 60.7631 | 60.6127 | 800 | 18.5588 | 8.5837 | 18.0426 | 7.9964 | 59.2276 | 52.9206 | 14.7628 | 14.3005 | 34.6848 | 33.0763 | 96.6996 | 96.8134 | 20.4802 | 19.8821 | 60.9143 | 60.7635 | 12.6009 | 8.7348 | 11.9933 | 8.1445 | 55.7747 | 53.6958
850 | 14.2105 | 13.991 | 16.2835 | 15.9329 | 105.0231 | 105.3298 | 850 | 12.8206 | 6.6202 | 14.7038 | 7.6069 | 108.1099 | 119.2154 | 19.0238 | 18.7846 | 10.046 | 9.6469 | 61.5322 | 61.5409 | 16.3292 | 15.9776 | 105.3181 | 105.6257 | 9.2788 | 6.7116 | 10.6973 | 7.7237 | 116.5437 | 120.5338
900 | 11.1204 | 11.033 | 11.3579 | 11.1511 | 38.6425 | 37.4219 | 900 | 9.8577 | 4.8581 | 9.9389 | 3.9834 | 42.0161 | 53.7906 | 8.2782 | 7.8483 | 7.4445 | 6.9236 | 27.4322 | 26.662 | 11.3937 | 11.1862 | 38.7642 | 37.5398 | 6.9776 | 4.9052 | 6.4875 | 4.0295 | 50.7091 | 54.1605
950 | 7.425 | 7.3504 | 7.7872 | 7.6911 | 23.8343 | 22.6246 | 950 | 6.5498 | 2.8538 | 6.8743 | 2.9651 | 27.2804 | 40.5974 | 9.7596 | 9.7422 | 3.7857 | 3.704 | 10.8221 | 10.0181 | 7.8145 | 7.7181 | 23.9179 | 22.704 | 4.2676 | 2.8666 | 4.5138 | 2.9972 | 36.6295 | 40.6844
1000 | 4.8523 | 4.8231 | 4.8272 | 4.7896 | 14.2883 | 13.56 | 1000 | 4.2605 | 1.7517 | 4.2473 | 1.7757 | 17.3681 | 30.4611 | 11.1766 | 11.1127 | 1.5442 | 1.5004 | 5.3084 | 4.8578 | 4.846 | 4.8083 | 14.3439 | 13.6128 | 2.7034 | 1.7656 | 2.7135 | 1.7961 | 25.9814 | 30.2816
1050 | 2.6357 | 2.6321 | 2.5751 | 2.5704 | 11.4197 | 12.4133 | 1050 | 2.3292 | 1.0551 | 2.3226 | 1.288 | 11.4643 | 16.1497 | 2.9269 | 2.9231 | 0.56367 | 0.55918 | 1.3017 | 1.1284 | 2.5861 | 2.5814 | 11.4686 | 12.4666 | 1.5248 | 1.0591 | 1.6368 | 1.29 | 14.739 | 16.0646
1100 | 1.6997 | 1.7016 | 1.8312 | 1.8324 | 8.2499 | 8.2503 | 1100 | 1.5006 | 0.64112 | 1.7966 | 1.6484 | 8.4629 | 9.8771 | 1.1806 | 1.1839 | 0.35388 | 0.3503 | 1.6861 | 1.6788 | 1.8398 | 1.841 | 8.2888 | 8.2892 | 0.95431 | 0.63719 | 1.6437 | 1.578 | 9.5364 | 9.932
1150 | 2.8241 | 2.8284 | 2.8431 | 2.8541 | 14.0853 | 12.3821 | 1150 | 2.6181 | 1.6508 | 2.5725 | 1.5058 | 17.4179 | 31.2964 | 1.7433 | 1.7133 | 0.29972 | 0.29122 | 0.83534 | 0.60981 | 2.8578 | 2.8688 | 14.1578 | 12.4459 | 2.0243 | 1.6298 | 1.9127 | 1.4952 | 26.2285 | 31.0443
1200 | 4.5457 | 4.5628 | 4.6358 | 4.6696 | 30.9297 | 25.2659 | 1200 | 4.1124 | 2.1716 | 4.0601 | 1.6723 | 37.1371 | 50.0163 | 1.955 | 1.9496 | 0.27479 | 0.28534 | 0.96778 | 1.554 | 4.6618 | 4.6958 | 31.1032 | 25.4076 | 2.8465 | 2.1297 | 2.4528 | 1.654 | 55.2516 | 49.3055
1250 | 6.3562 | 6.3721 | 6.5658 | 6.6022 | 21.6665 | 14.6874 | 1250 | 5.8924 | 3.632 | 5.9546 | 3.1153 | 30.6727 | 54.8335 | 1.893 | 1.9715 | 0.18816 | 0.19605 | 0.41419 | 0.72539 | 6.6057 | 6.6424 | 21.7984 | 14.7767 | 4.4463 | 3.5459 | 4.1375 | 3.0572 | 53.2713 | 53.7413
1300 | 8.1081 | 8.1176 | 8.5172 | 8.5507 | 9.8085 | 6.8801 | 1300 | 7.6314 | 5.0781 | 7.9031 | 4.7507 | 17.4578 | 40.9128 | 2.0178 | 2.1107 | 0.24283 | 0.24025 | 1.0718 | 1.1689 | 8.5733 | 8.607 | 9.8731 | 6.9254 | 6.0861 | 4.9358 | 5.9776 | 4.6286 | 38.1605 | 39.8804
1350 | 9.8122 | 9.8293 | 10.5571 | 10.583 | 6.903 | 5.7995 | 1350 | 9.2061 | 5.8891 | 9.9189 | 6.4341 | 15.5041 | 38.9336 | 2.9256 | 2.8699 | 1.1176 | 1.0732 | 1.325 | 0.95801 | 10.6321 | 10.6581 | 6.952 | 5.8407 | 7.1756 | 5.6975 | 7.755 | 6.2339 | 39.06 | 37.717
1400 | 11.4009 | 11.4397 | 12.4996 | 12.5407 | 4.6542 | 8.3667 | 1400 | 10.4588 | 5.992 | 11.559 | 7.0499 | 11.8381 | 37.5543 | 2.6094 | 2.5694 | 3.274 | 3.1676 | 2.2044 | 2.335 | 12.5951 | 12.6366 | 4.6898 | 8.4306 | 8.157 | 5.7627 | 9.13 | 6.7858 | 35.7931 | 36.1735
1450 | 13.1243 | 13.236 | 14.2106 | 14.3541 | 4.6953 | 12.5185 | 1450 | 11.8579 | 5.9658 | 12.8826 | 6.6983 | 7.4434 | 36.2996 | 2.5335 | 2.5333 | 6.7143 | 6.7291 | 2.8995 | 6.5408 | 14.3272 | 14.4718 | 4.7338 | 12.6211 | 7.8544 | 5.7197 | 8.6323 | 6.4186 | 32.8968 | 34.7702
1500 | 14.996 | 15.0289 | 16.3506 | 16.4309 | 9.3531 | 18.2878 | 1500 | 13.983 | 8.4667 | 15.2127 | 9.3161 | 6.3396 | 36.6801 | 2.4193 | 2.4145 | 4.5867 | 4.4506 | 3.8876 | 6.0046 | 16.4942 | 16.5752 | 9.4353 | 18.4484 | 10.4919 | 8.0569 | 11.3117 | 8.8613 | 31.3989 | 34.9445
1550 | 16.9664 | 16.9576 | 18.9355 | 18.9578 | 11.2974 | 22.9047 | 1550 | 16.0631 | 10.6816 | 17.9301 | 11.9814 | 3.8302 | 40.2403 | 2.368 | 2.3647 | 4.0695 | 3.8303 | 2.4544 | 3.5642 | 19.1131 | 19.1357 | 11.4034 | 23.1196 | 12.4314 | 10.1195 | 13.9244 | 11.3386 | 31.9837 | 38.1031
1600 | 19.1377 | 19.001 | 20.9918 | 20.9742 | 13.6605 | 27.5167 | 1600 | 18.6855 | 14.7426 | 20.101 | 14.051 | 4.2132 | 44.4359 | 2.092 | 2.1305 | 7.8251 | 7.3286 | 4.268 | 4.9954 | 21.2018 | 21.184 | 13.7972 | 27.792 | 15.8678 | 13.8484 | 16.1401 | 13.2678 | 33.0866 | 41.711
1650 | 21.0881 | 20.8121 | 24.0389 | 23.7786 | 16.5785 | 33.3147 | 1650 | 20.7455 | 16.8395 | 23.5802 | 18.739 | 5.804 | 49.6246 | 2.5352 | 2.4731 | 5.4504 | 5.0276 | 1.2432 | 3.045 | 24.2948 | 24.0317 | 16.755 | 33.6693 | 18.2507 | 15.7613 | 20.5574 | 17.5448 | 34.5071 | 46.3418
1700 | 23.1063 | 22.1369 | 26.0752 | 25.6691 | 28.921 | 58.8846 | 1700 | 23.3215 | 20.024 | 24.9818 | 17.8218 | 11.7131 | 62.8206 | 2.6075 | 2.1815 | 2.8771 | 2.3 | 2.7371 | 6.1121 | 26.37 | 25.9593 | 29.248 | 59.5503 | 24.0311 | 18.5511 | 22.9752 | 16.5521 | 38.7917 | 58.2621
1750 | 23.7474 | 24.0814 | 28.3086 | 28.8914 | 14.4832 | 24.4692 | 1750 | 21.1831 | 10.1472 | 25.2731 | 11.7805 | 8.1853 | 40.8747 | 1.8172 | 1.9978 | 2.5948 | 2.6707 | 1.5126 | 2.7985 | 28.648 | 29.2377 | 14.6568 | 24.7625 | 13.6204 | 9.358 | 15.924 | 10.9055 | 30.3025 | 37.8012
1800 | 26.8277 | 26.7317 | 32.9802 | 32.9675 | 19.3072 | 33.8881 | 1800 | 25.2674 | 15.8282 | 31.1907 | 19.6819 | 5.9261 | 46.0824 | 1.9695 | 2.0248 | 4.0766 | 4.079 | 2.0545 | 3.8995 | 33.3987 | 33.3859 | 19.5522 | 34.3182 | 18.7889 | 14.4703 | 22.9969 | 18.0551 | 32.2966 | 42.2105
1850 | 29.3181 | 29.0464 | 37.1714 | 36.8156 | 20.9569 | 35.5953 | 1850 | 27.8454 | 18.3608 | 35.6459 | 24.2788 | 8.0998 | 46.3966 | 1.3123 | 1.6254 | 3.8465 | 3.8895 | 5.0056 | 7.5294 | 37.6701 | 37.3095 | 21.2381 | 36.0728 | 21.6378 | 16.6893 | 28.109 | 22.0952 | 31.8709 | 42.1559
1900 | 32.2935 | 31.8542 | 42.6701 | 42.0641 | 26.5494 | 52.4373 | 1900 | 31.159 | 22.0706 | 41.6278 | 30.9113 | 8.884 | 65.7446 | 2.447 | 2.5138 | 4.6275 | 4.5602 | 3.9489 | 7.4043 | 43.2743 | 42.6597 | 26.9254 | 53.1798 | 24.4847 | 19.8622 | 33.2534 | 27.8797 | 37.7337 | 59.2233
1950 | 34.8158 | 34.4517 | 50.6372 | 47.7627 | 42.429 | 94.5494 | 1950 | 33.2847 | 21.8819 | 52.0673 | 48.8608 | 17.6998 | 99.0754 | 2.8373 | 2.727 | 4.2156 | 3.9795 | 5.0268 | 10.7073 | 51.393 | 48.4756 | 43.0623 | 95.9606 | 25.0888 | 19.7398 | 49.4925 | 43.6661 | 47.6308 | 88.5093
2000 | 40.5148 | 39.3336 | 55.9759 | 54.2178 | 32.818 | 42.7257 | 2000 | 41.3354 | 39.0404 | 55.4246 | 43.6074 | 16.9915 | 42.0373 | 2.2689 | 2.2847 | 3.6731 | 3.5998 | 3.6057 | 4.361 | 56.8554 | 55.0698 | 33.3337 | 43.3971 | 37.0602 | 34.9026 | 46.2777 | 38.8135 | 32.9118 | 37.2195

## Cruiserath 220 kV
Terminal | Cruiserath 220 kV |  |  |  | Terminal | Cruiserath 220 kV
Terminal Name | Cruiserath 220 kV |  |  |  | Terminal Name | Cruiserath 220 kV_Clonee 220 kV |  |  |  | Cruiserath 220 kV_Corduff 110 kV |  |  |  | Cruiserath 220 kV_Corduff 220 kV |  |  |  | Cruiserath 220 kV_Woodland 220 kV
Study Case | step1 |  | step2 |  | Study Case | step1 |  | step2 |  | step1 |  | step2 |  | step1 |  | step2 |  | step1 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  |  |  | Filter Details
Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  |  |  | Frequency in Hz
50 | 8.2905 | 9.224 | 6.9407 | 7.148 | 50 | 7.6244 | 5.7421 | 6.5244 | 5.5935 | 3.2038 | 3.4224 | 2.8182 | 2.8718 | 8.188 | 9.1214 | 6.8381 | 7.0453 | 6.2256 | 5.7842 | 5.7758 | 5.6356
100 | 20.9736 | 23.3172 | 19.429 | 19.9374 | 100 | 19.5475 | 15.6816 | 18.5569 | 16.6144 | 8.4653 | 9.0353 | 8.2883 | 8.4253 | 20.7757 | 23.1185 | 19.2348 | 19.7425 | 16.6195 | 15.8686 | 17.0643 | 16.8134
150 | 46.6128 | 50.9711 | 33.4782 | 33.9335 | 150 | 45.0494 | 41.9469 | 33.3502 | 33.2211 | 21.252 | 22.434 | 16.3167 | 16.4827 | 46.5109 | 50.8636 | 33.5422 | 33.9917 | 42.0718 | 42.5293 | 33.4089 | 33.6621
200 | 9.8857 | 12.764 | 5.4621 | 5.8228 | 200 | 9.0934 | 11.3602 | 5.407 | 6.9405 | 4.7792 | 4.8399 | 3.2467 | 3.1788 | 9.7853 | 12.571 | 5.439 | 5.7398 | 9.7956 | 11.4415 | 6.5214 | 6.9627
250 | 20.2022 | 26.8616 | 13.8644 | 15.6245 | 250 | 16.8347 | 8.7875 | 11.6832 | 7.4406 | 5.6159 | 7.1882 | 3.9302 | 4.2952 | 19.829 | 26.4966 | 13.4576 | 15.2089 | 10.323 | 8.9926 | 8.0785 | 7.7622
300 | 70.1688 | 106.9796 | 31.8208 | 35.9832 | 300 | 62.4964 | 47.0321 | 28.5876 | 21.5955 | 21.6985 | 32.1823 | 9.4381 | 10.5365 | 69.8217 | 106.7443 | 31.6619 | 35.8573 | 46.4505 | 48.9665 | 22.2866 | 22.4827
350 | 47.2486 | 44.2805 | 19.9744 | 20.042 | 350 | 40.8372 | 15.4255 | 18.5752 | 12.7816 | 17.3146 | 15.7061 | 7.3434 | 7.2714 | 47.6424 | 44.8525 | 20.4342 | 20.532 | 26.1721 | 15.9921 | 14.716 | 13.2702
400 | 14.6361 | 13.4887 | 4.8425 | 4.7857 | 400 | 13.0984 | 4.5824 | 4.4394 | 2.1459 | 6.3381 | 5.618 | 2.1567 | 2.0892 | 15.326 | 14.2 | 5.1483 | 5.1074 | 7.6938 | 4.7313 | 2.8175 | 2.2303
450 | 5.9277 | 6.0371 | 11.1147 | 11.2953 | 450 | 4.6409 | 2.0709 | 9.4096 | 6.6143 | 2.4611 | 2.4254 | 5.2232 | 5.2261 | 5.3181 | 5.4295 | 10.262 | 10.4416 | 3.0155 | 2.1395 | 7.4813 | 6.8166
500 | 22.1888 | 23.8172 | 32.2871 | 33.4834 | 500 | 18.7992 | 9.881 | 29.6053 | 23.125 | 11.6885 | 12.0282 | 18.4367 | 18.7081 | 21.2242 | 22.8497 | 31.7829 | 32.9837 | 13.0305 | 10.1595 | 24.9772 | 23.797
550 | 49.9313 | 59.3315 | 7.4355 | 7.5123 | 550 | 43.4283 | 26.0268 | 5.8624 | 3.9459 | 28.0874 | 31.323 | 4.3312 | 4.2256 | 48.9987 | 58.387 | 6.4274 | 6.5016 | 30.4985 | 26.6632 | 4.5735 | 4.0326
600 | 72.4645 | 99.7161 | 19.1398 | 19.6472 | 600 | 62.1608 | 36.7495 | 16.2664 | 10.853 | 30.7734 | 41.8034 | 8.3299 | 8.7511 | 72.0094 | 99.4902 | 17.9465 | 18.449 | 40.5362 | 37.5741 | 12.4824 | 11.1984
650 | 90.2181 | 72.7694 | 29.6775 | 29.9346 | 650 | 77.3832 | 20.0379 | 26.952 | 22.006 | 49.4698 | 41.0854 | 12.8715 | 13.0363 | 90.9366 | 73.7291 | 28.3869 | 28.639 | 43.7743 | 20.7001 | 23.7834 | 22.4634
700 | 39.39 | 35.7629 | 42.9214 | 44.1157 | 700 | 35.3743 | 12.9401 | 39.1954 | 31.8566 | 30.6596 | 28.2191 | 32.3448 | 33.275 | 40.6303 | 37.0336 | 41.7176 | 42.8779 | 22.2815 | 13.2654 | 34.1254 | 32.5114
750 | 24.6637 | 23.3831 | 44.9905 | 46.2565 | 750 | 22.4417 | 8.4192 | 40.8185 | 30.7461 | 36.8023 | 34.2476 | 61.558 | 63.4162 | 25.9262 | 24.684 | 43.9074 | 45.1753 | 13.7226 | 8.6264 | 33.5242 | 31.2948
800 | 19.125 | 18.4993 | 61.7108 | 61.5692 | 800 | 18.0875 | 8.0163 | 59.3749 | 53.0523 | 34.763 | 33.1517 | 96.9344 | 97.0495 | 20.4802 | 19.8821 | 60.9143 | 60.7635 | 12.0232 | 8.1648 | 55.9135 | 53.8295
850 | 14.7255 | 14.3655 | 104.468 | 104.8065 | 850 | 14.7451 | 7.6282 | 108.4136 | 119.5503 | 10.0782 | 9.6766 | 61.7283 | 61.7382 | 16.3292 | 15.9776 | 105.3181 | 105.6257 | 10.7274 | 7.7454 | 116.8712 | 120.8724
900 | 9.7076 | 9.4855 | 37.3277 | 36.1132 | 900 | 9.9702 | 3.9959 | 42.1484 | 53.96 | 7.4655 | 6.9427 | 27.557 | 26.7861 | 11.3937 | 11.1862 | 38.7642 | 37.5398 | 6.5079 | 4.0422 | 50.8688 | 54.3311
950 | 6.0364 | 5.9333 | 22.335 | 21.2006 | 950 | 6.8984 | 2.9755 | 27.3762 | 40.7399 | 3.7919 | 3.7125 | 10.8011 | 9.9859 | 7.8145 | 7.7181 | 23.9179 | 22.704 | 4.5296 | 3.0077 | 36.7581 | 40.8272
1000 | 3.1124 | 3.0703 | 12.6868 | 12.1156 | 1000 | 4.2638 | 1.7826 | 17.4357 | 30.5796 | 1.548 | 1.5036 | 5.3411 | 4.8933 | 4.846 | 4.8083 | 14.3439 | 13.6128 | 2.7241 | 1.8031 | 26.0824 | 30.3994
1050 | 1.7777 | 1.7702 | 10.3675 | 11.4392 | 1050 | 2.3325 | 1.2935 | 11.5135 | 16.2189 | 0.56514 | 0.56051 | 1.3347 | 1.1551 | 2.5861 | 2.5814 | 11.4686 | 12.4666 | 1.6438 | 1.2956 | 14.8023 | 16.1335
1100 | 3.1362 | 3.1386 | 8.385 | 8.4263 | 1100 | 1.805 | 1.6562 | 8.5027 | 9.9236 | 0.3702 | 0.36623 | 1.6763 | 1.6718 | 1.8398 | 1.841 | 8.2888 | 8.2892 | 1.6514 | 1.5855 | 9.5813 | 9.9788
1150 | 4.9362 | 4.9487 | 15.495 | 13.7012 | 1150 | 2.5857 | 1.5135 | 17.5075 | 31.4575 | 0.29564 | 0.28726 | 0.85158 | 0.62247 | 2.8578 | 2.8688 | 14.1578 | 12.4459 | 1.9225 | 1.5029 | 26.3635 | 31.2041
1200 | 7.008 | 7.0417 | 31.5762 | 26.141 | 1200 | 4.0829 | 1.6816 | 37.3453 | 50.2968 | 0.27882 | 0.28934 | 0.97006 | 1.562 | 4.6618 | 4.6958 | 31.1032 | 25.4076 | 2.4665 | 1.6633 | 55.5614 | 49.5819
1250 | 9.1076 | 9.1445 | 19.9472 | 13.222 | 1250 | 5.9909 | 3.1343 | 30.8594 | 55.1672 | 0.18912 | 0.19712 | 0.41918 | 0.73309 | 6.6057 | 6.6424 | 21.7984 | 14.7767 | 4.1626 | 3.0758 | 53.5955 | 54.0684
1300 | 11.2076 | 11.2428 | 8.2894 | 7.2472 | 1300 | 7.9552 | 4.782 | 17.5728 | 41.1822 | 0.24459 | 0.24191 | 1.0809 | 1.1782 | 8.5733 | 8.607 | 9.8731 | 6.9254 | 6.017 | 4.659 | 38.4118 | 40.143
1350 | 13.3953 | 13.4229 | 5.6339 | 7.5464 | 1350 | 9.9894 | 6.4798 | 15.6142 | 39.2102 | 1.125 | 1.0803 | 1.3307 | 0.95928 | 10.6321 | 10.6581 | 6.952 | 5.8407 | 7.8101 | 6.2782 | 39.3375 | 37.9849
1400 | 15.4719 | 15.5216 | 4.9749 | 10.8382 | 1400 | 11.6473 | 7.1038 | 11.9286 | 37.8414 | 3.2991 | 3.1924 | 2.2367 | 2.372 | 12.5951 | 12.6366 | 4.6898 | 8.4306 | 9.1998 | 6.8377 | 36.0667 | 36.45
1450 | 17.3341 | 17.4821 | 7.2101 | 15.4885 | 1450 | 12.9883 | 6.7533 | 7.5045 | 36.5973 | 6.771 | 6.7856 | 2.935 | 6.6058 | 14.3272 | 14.4718 | 4.7338 | 12.6211 | 8.7032 | 6.4713 | 33.1666 | 35.0555
1500 | 19.6347 | 19.7204 | 11.9824 | 21.3492 | 1500 | 15.3463 | 9.3979 | 6.3952 | 37.0023 | 4.642 | 4.5018 | 3.9291 | 6.0425 | 16.4942 | 16.5752 | 9.4353 | 18.4484 | 11.4111 | 8.9391 | 31.6747 | 35.2514
1550 | 22.3905 | 22.4165 | 14.4282 | 26.3212 | 1550 | 18.0983 | 12.0938 | 3.8662 | 40.6178 | 4.1008 | 3.8592 | 2.4456 | 3.5703 | 19.1131 | 19.1357 | 11.4034 | 23.1196 | 14.055 | 11.445 | 32.2838 | 38.4606
1600 | 24.6124 | 24.5984 | 16.9194 | 31.1053 | 1600 | 20.3021 | 14.1916 | 4.2553 | 44.8804 | 7.8931 | 7.3933 | 4.3076 | 5.0689 | 21.2018 | 21.184 | 13.7972 | 27.792 | 16.3015 | 13.4005 | 33.4176 | 42.1282
1650 | 27.8491 | 27.59 | 19.8305 | 36.9001 | 1650 | 23.8312 | 18.9384 | 5.8658 | 50.1528 | 5.4985 | 5.0783 | 1.2312 | 3.0997 | 24.2948 | 24.0317 | 16.755 | 33.6693 | 20.7762 | 17.7316 | 34.8744 | 46.835
1700 | 30.0285 | 29.6485 | 32.4133 | 62.5013 | 1700 | 25.2642 | 18.0233 | 11.8456 | 63.5309 | 2.9423 | 2.3461 | 2.6609 | 6.0183 | 26.37 | 25.9593 | 29.248 | 59.5503 | 23.235 | 16.7392 | 39.2303 | 58.9208
1750 | 32.4906 | 33.101 | 16.7367 | 26.6916 | 1750 | 25.5761 | 11.9218 | 8.2834 | 41.3647 | 2.5668 | 2.6609 | 1.7216 | 3.0713 | 28.648 | 29.2377 | 14.6568 | 24.7625 | 16.1149 | 11.0362 | 30.6658 | 38.2543
1800 | 37.4309 | 37.4248 | 22.9633 | 37.5339 | 1800 | 31.5866 | 19.9316 | 6.0013 | 46.6672 | 4.1285 | 4.1369 | 2.0748 | 3.9299 | 33.3987 | 33.3859 | 19.5522 | 34.3182 | 23.2887 | 18.2843 | 32.7065 | 42.7462
1850 | 41.8635 | 41.5155 | 24.4968 | 39.1202 | 1850 | 36.1241 | 24.6045 | 8.2084 | 47.019 | 3.9369 | 3.9552 | 4.9525 | 7.4643 | 37.6701 | 37.3095 | 21.2381 | 36.0728 | 28.4861 | 22.3916 | 32.2985 | 42.7215
1900 | 47.6886 | 47.0749 | 30.9286 | 57.2527 | 1900 | 42.2173 | 31.349 | 9.0098 | 66.6756 | 4.6933 | 4.6258 | 4.0783 | 7.6249 | 43.2743 | 42.6597 | 26.9254 | 53.1798 | 33.7243 | 28.2745 | 38.268 | 60.0619
1950 | 55.9968 | 53.0621 | 47.2599 | 99.8394 | 1950 | 52.8445 | 49.5902 | 17.964 | 100.5543 | 4.2898 | 4.0452 | 5.046 | 10.763 | 51.393 | 48.4756 | 43.0623 | 95.9606 | 50.2313 | 44.3179 | 48.3418 | 89.8304
2000 | 61.7067 | 59.9198 | 34.9623 | 43.6184 | 2000 | 56.2955 | 44.2926 | 17.2585 | 42.6979 | 3.7043 | 3.6315 | 3.5929 | 4.3564 | 56.8554 | 55.0698 | 33.3337 | 43.3971 | 47.0049 | 39.4233 | 33.4289 | 37.8044

## Woodland 220 kV
Terminal | Woodland 220 kV | [5 empty] | Terminal | Woodland 220 kV
Terminal Name | Woodland 220 kV | [5 empty] | Terminal Name | Woodland 220 kV_Clonee 220 kV | [5 empty] | Woodland 220 kV_Corduff 110 kV | [5 empty] | Woodland 220 kV_Corduff 220 kV | [5 empty] | Woodland 220 kV_Cruiserath 220 kV
Study Case | step0 |  | step1 |  | step2 |  | Study Case | step0 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2 |  | step0 |  | step1 |  | step2 |  | step1 |  | step2
Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details | [6 empty] | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step2_Base_Case | step2_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | m:Z | m:Z | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz | [6 empty] | Frequency in Hz
50 | 7.3678 | 7.613 | 7.3598 | 7.6181 | 6.5671 | 6.6602 | 50 | 6.5262 | 7.5388 | 6.5241 | 7.5443 | 5.9809 | 6.6027 | 2.6333 | 2.4964 | 2.6391 | 2.4797 | 2.5462 | 2.5098 | 6.2255 | 5.7526 | 6.2256 | 5.7842 | 5.7758 | 5.6356 | 6.2256 | 5.7842 | 5.7758 | 5.6356
100 | 18.1749 | 18.4956 | 18.5228 | 18.8755 | 18.4118 | 18.5199 | 100 | 16.6848 | 18.2328 | 17.0807 | 18.6122 | 17.3733 | 18.2833 | 7.0041 | 6.7447 | 7.2425 | 6.9292 | 7.7179 | 7.6476 | 16.2037 | 15.3368 | 16.6189 | 15.868 | 17.0637 | 16.8127 | 16.6195 | 15.8686 | 17.0643 | 16.8134
150 | 41.0549 | 40.1592 | 40.6549 | 39.5428 | 31.8353 | 31.4298 | 150 | 41.2195 | 39.5357 | 41.4618 | 38.9642 | 32.8234 | 31.0221 | 19.0039 | 18.8693 | 19.6401 | 19.4162 | 16.1224 | 16.1556 | 41.5802 | 41.4764 | 42.0681 | 42.5256 | 33.406 | 33.6592 | 42.0718 | 42.5293 | 33.4089 | 33.6621
200 | 8.995 | 8.31 | 7.2964 | 6.9677 | 4.7174 | 4.535 | 200 | 10.8285 | 8.1579 | 8.7799 | 6.7977 | 5.8704 | 4.4763 | 6.43 | 6.8301 | 5.6266 | 6.0237 | 3.8566 | 3.9674 | 11.8879 | 13.4152 | 9.794 | 11.4397 | 6.5203 | 6.9616 | 9.7956 | 11.4415 | 6.5214 | 6.9627
250 | 12.8662 | 13.4796 | 13.2884 | 14.2747 | 9.8013 | 9.9124 | 250 | 11.2075 | 12.9283 | 10.6325 | 13.6815 | 8.3231 | 9.4634 | 4.5204 | 4.5476 | 3.7729 | 3.6933 | 3.1156 | 3.1142 | 11.3974 | 10.6412 | 10.3204 | 8.9904 | 8.0765 | 7.7603 | 10.323 | 8.9926 | 8.0785 | 7.7622
300 | 36.82 | 32.9411 | 39.6281 | 32.85 | 17.1433 | 15.1576 | 300 | 38.8092 | 31.6721 | 43.9383 | 31.5902 | 20.4562 | 14.5536 | 12.1892 | 12.6577 | 15.0654 | 15.7701 | 7.2416 | 7.3249 | 40.3344 | 41.03 | 46.4341 | 48.9493 | 22.2788 | 22.4748 | 46.4505 | 48.9665 | 22.2866 | 22.4827
350 | 9.415 | 13.5935 | 7.9323 | 13.7928 | 5.6203 | 6.0759 | 350 | 22.0156 | 13.1583 | 20.0719 | 13.3549 | 11.246 | 5.8943 | 9.2742 | 5.4786 | 9.2893 | 5.1603 | 5.185 | 4.5057 | 28.1557 | 17.6727 | 26.1596 | 15.9845 | 14.709 | 13.2639 | 26.1721 | 15.9921 | 14.716 | 13.2702
400 | 11.4679 | 17.9021 | 11.8163 | 18.5794 | 11.074 | 13.9343 | 400 | 3.5939 | 17.361 | 3.4143 | 18.0235 | 3.0732 | 13.5247 | 2.6025 | 1.4687 | 2.8622 | 1.6536 | 1.8968 | 1.9606 | 7.8033 | 4.7708 | 7.689 | 4.7283 | 2.8158 | 2.2289 | 7.6938 | 4.7313 | 2.8175 | 2.2303
450 | 20.2363 | 26.7642 | 20.2219 | 26.7337 | 19.0803 | 21.5574 | 450 | 7.2068 | 25.9482 | 7.2033 | 25.9174 | 10.5357 | 20.9127 | 2.2466 | 2.2873 | 2.6646 | 2.7121 | 5.5258 | 5.5773 | 2.9963 | 2.1259 | 3.0131 | 2.1379 | 7.4754 | 6.8112 | 3.0155 | 2.1395 | 7.4813 | 6.8166
500 | 29.7172 | 35.5544 | 29.8724 | 35.5457 | 28.798 | 29.3925 | 500 | 17.0132 | 34.5381 | 17.4175 | 34.5331 | 25.2973 | 28.5709 | 7.2206 | 6.5575 | 9.2917 | 8.3973 | 17.2771 | 17.0227 | 12.4529 | 9.6679 | 13.0178 | 10.1496 | 24.953 | 23.7739 | 13.0305 | 10.1595 | 24.9772 | 23.797
550 | 40.3773 | 42.6375 | 38.8067 | 40.8962 | 21.4908 | 26.0394 | 550 | 32.267 | 41.5944 | 32.2245 | 39.8771 | 9.0502 | 25.4114 | 16.5694 | 15.1905 | 20.9962 | 19.2493 | 8.2037 | 9.2891 | 29.676 | 25.2461 | 30.4626 | 26.6319 | 4.5681 | 4.0278 | 30.4985 | 26.6632 | 4.5735 | 4.0326
600 | 40.9949 | 34.3645 | 30.4943 | 27.4321 | 27.0639 | 29.8784 | 600 | 47.4473 | 33.5142 | 36.2668 | 26.7221 | 16.3956 | 29.0851 | 24.6116 | 25.234 | 23.7441 | 24.8673 | 6.9948 | 7.3724 | 51.288 | 49.3737 | 40.4795 | 37.5216 | 12.465 | 11.1827 | 40.5362 | 37.5741 | 12.4824 | 11.1984
650 | 16.8421 | 27.7398 | 19.3755 | 32.2398 | 40.884 | 44.5065 | 650 | 29.6501 | 27.1257 | 32.6776 | 31.5626 | 28.3551 | 43.5446 | 15.5259 | 14.8139 | 27.7246 | 17.0294 | 10.6368 | 10.1805 | 39.0016 | 26.6486 | 43.7025 | 20.6662 | 23.7443 | 22.4265 | 43.7743 | 20.7001 | 23.7834 | 22.4634
700 | 17.5334 | 38.0859 | 20.4588 | 39.2779 | 45.1507 | 46.8682 | 700 | 17.5433 | 37.3713 | 12.2413 | 38.6073 | 36.8609 | 45.8951 | 15.2096 | 9.3691 | 19.6417 | 14.3657 | 26.368 | 25.1077 | 29.0121 | 15.1576 | 22.2391 | 13.2402 | 34.0605 | 32.4496 | 22.2815 | 13.2654 | 34.1254 | 32.5114
750 | 22.3295 | 39.145 | 24.4993 | 39.0743 | 44.3479 | 46.5326 | 750 | 7.507 | 38.4229 | 6.1356 | 38.2732 | 35.7291 | 45.677 | 10.7133 | 6.6997 | 19.4819 | 12.0528 | 49.6934 | 47.5174 | 17.3215 | 11.4266 | 13.6927 | 8.6075 | 33.451 | 31.2265 | 13.7226 | 8.6264 | 33.5242 | 31.2948
800 | 28.0923 | 46.2365 | 29.4951 | 47.0197 | 69.8793 | 74.8528 | 800 | 2.4632 | 45.4528 | 5.1255 | 46.2332 | 58.5517 | 73.7716 | 9.3982 | 6.8972 | 22.7557 | 16.9941 | 91.6365 | 89.4348 | 12.6009 | 8.7348 | 11.9933 | 8.1445 | 55.7747 | 53.6958 | 12.0232 | 8.1648 | 55.9135 | 53.8295
850 | 35.6059 | 57.6394 | 34.6265 | 57.1426 | 107.4411 | 109.4846 | 850 | 4.121 | 56.9014 | 3.1476 | 56.4365 | 113.5175 | 108.2911 | 13.1574 | 10.072 | 6.9752 | 5.2827 | 69.4623 | 71.9911 | 9.2788 | 6.7116 | 10.6973 | 7.7237 | 116.5437 | 120.5338 | 10.7274 | 7.7454 | 116.8712 | 120.8724
900 | 37.4583 | 56.3822 | 38.9277 | 58.948 | 33.0213 | 32.3304 | 900 | 5.6343 | 55.9183 | 6.4974 | 58.5052 | 44.9197 | 32.1471 | 3.7737 | 6.6285 | 6.4509 | 8.9754 | 35.4144 | 37.751 | 6.9776 | 4.9052 | 6.4875 | 4.0295 | 50.7091 | 54.1605 | 6.5079 | 4.0422 | 50.8688 | 54.3311
950 | 39.8026 | 58.2994 | 40.3118 | 59.4087 | 12.7352 | 12.9689 | 950 | 8.3366 | 58.0619 | 8.3209 | 59.2525 | 28.9727 | 12.9065 | 7.983 | 7.1143 | 3.7022 | 3.5679 | 18.2262 | 20.475 | 4.2676 | 2.8666 | 4.5138 | 2.9972 | 36.6295 | 40.6844 | 4.5296 | 3.0077 | 36.7581 | 40.8272
1000 | 42.7204 | 61.4322 | 43.3848 | 62.4164 | 13.9438 | 26.5867 | 1000 | 10.3633 | 61.4099 | 10.6045 | 62.5294 | 16.5404 | 26.6282 | 9.9167 | 10.0925 | 1.5287 | 1.7381 | 8.886 | 10.1791 | 2.7034 | 1.7656 | 2.7135 | 1.7961 | 25.9814 | 30.2816 | 2.7241 | 1.8031 | 26.0824 | 30.3994
1050 | 43.8246 | 60.4335 | 42.3494 | 57.3773 | 26.5073 | 40.0159 | 1050 | 11.634 | 60.5806 | 11.3215 | 57.5251 | 6.2373 | 40.166 | 5.1769 | 6.228 | 1.9713 | 2.4715 | 4.6145 | 5.6866 | 1.5248 | 1.0591 | 1.6368 | 1.29 | 14.739 | 16.0646 | 1.6438 | 1.2956 | 14.8023 | 16.1335
1100 | 48.3036 | 68.343 | 47.927 | 67.2399 | 48.1934 | 69.8529 | 1100 | 13.8003 | 68.8036 | 13.7137 | 67.632 | 14.8422 | 70.0381 | 1.5282 | 2.6791 | 1.543 | 2.1417 | 3.2973 | 4.1363 | 0.95431 | 0.63719 | 1.6437 | 1.578 | 9.5364 | 9.932 | 1.6514 | 1.5855 | 9.5813 | 9.9788
1150 | 54.1939 | 76.0625 | 50.768 | 69.5241 | 104.8048 | 161.1606 | 1150 | 16.6095 | 77.0332 | 15.4077 | 70.1099 | 46.6461 | 162.5081 | 5.706 | 7.6458 | 0.60592 | 0.70786 | 4.025 | 5.8407 | 2.0243 | 1.6298 | 1.9127 | 1.4952 | 26.2285 | 31.0443 | 1.9225 | 1.5029 | 26.3635 | 31.2041
1200 | 54.3688 | 76.0158 | 48.9641 | 66.0535 | 107.8367 | 111.2703 | 1200 | 17.4526 | 77.4513 | 15.5295 | 67.0002 | 70.3693 | 112.8922 | 10.0712 | 13.8153 | 1.1229 | 1.5811 | 2.0268 | 2.2473 | 2.8465 | 2.1297 | 2.4528 | 1.654 | 55.2516 | 49.3055 | 2.4665 | 1.6633 | 55.5614 | 49.5819
1250 | 62.6493 | 90.9371 | 59.8496 | 85.1683 | 60.5963 | 65.6017 | 1250 | 21.002 | 93.0027 | 19.9366 | 86.9091 | 54.9449 | 66.943 | 3.9372 | 6.5058 | 0.51681 | 0.83413 | 1.1003 | 1.1156 | 4.4463 | 3.5459 | 4.1375 | 3.0572 | 53.2713 | 53.7413 | 4.1626 | 3.0758 | 53.5955 | 54.0684
1300 | 72.6147 | 109.3583 | 70.0166 | 103.4505 | 45.2156 | 53.7511 | 1300 | 25.1257 | 112.4889 | 24.2745 | 106.2261 | 37.5455 | 55.1547 | 3.4734 | 6.3854 | 1.169 | 1.7761 | 0.60009 | 0.64446 | 6.0861 | 4.9358 | 5.9776 | 4.6286 | 38.1605 | 39.8804 | 6.017 | 4.659 | 38.4118 | 40.143
1350 | 76.7086 | 116.8055 | 75.7192 | 113.3448 | 52.8758 | 56.4603 | 1350 | 27.1723 | 120.7556 | 27.2713 | 116.9823 | 42.1399 | 58.2809 | 4.9661 | 6.2026 | 2.1103 | 2.68 | 3.8718 | 3.7271 | 7.1756 | 5.6975 | 7.755 | 6.2339 | 39.06 | 37.717 | 7.8101 | 6.2782 | 39.3375 | 37.9849
1400 | 76.6087 | 102.4853 | 77.6188 | 106.8806 | 34.7091 | 36.2889 | 1400 | 27.9803 | 106.6121 | 28.9271 | 111.0417 | 35.6396 | 37.6875 | 3.3528 | 3.4142 | 3.7649 | 3.7 | 9.4002 | 9.4386 | 8.157 | 5.7627 | 9.13 | 6.7858 | 35.7931 | 36.1735 | 9.1998 | 6.8377 | 36.0667 | 36.45
1450 | 66.4379 | 90.8023 | 66.2208 | 89.521 | 24.2387 | 25.1476 | 1450 | 24.8669 | 94.7785 | 25.3408 | 93.365 | 30.6671 | 26.2681 | 2.2758 | 2.2605 | 2.2424 | 2.2984 | 15.6718 | 16.5278 | 7.8544 | 5.7197 | 8.6323 | 6.4186 | 32.8968 | 34.7702 | 8.7032 | 6.4713 | 33.1666 | 35.0555
1500 | 81.2473 | 116.0931 | 78.9843 | 111.6236 | 15.2887 | 14.8 | 1500 | 31.2082 | 122.0962 | 31.0473 | 117.082 | 27.2435 | 15.5486 | 2.8188 | 3.4205 | 7.459 | 9.6687 | 7.5531 | 8.3465 | 10.4919 | 8.0569 | 11.3117 | 8.8613 | 31.3989 | 34.9445 | 11.4111 | 8.9391 | 31.6747 | 35.2514
1550 | 86.9444 | 127.715 | 89.1369 | 131.5018 | 8.2806 | 6.9237 | 1550 | 34.2852 | 134.6261 | 35.9725 | 138.6896 | 25.6288 | 7.2668 | 1.9315 | 1.8831 | 7.9283 | 10.3295 | 4.867 | 5.5166 | 12.4314 | 10.1195 | 13.9244 | 11.3386 | 31.9837 | 38.1031 | 14.055 | 11.445 | 32.2838 | 38.4606
1600 | 103.1079 | 161.6169 | 100.562 | 155.2833 | 4.3445 | 6.8282 | 1600 | 41.6915 | 171.9024 | 41.0401 | 164.8635 | 24.8796 | 7.2646 | 0.48688 | 1.6865 | 15.0332 | 20.1092 | 10.1964 | 11.6367 | 15.8678 | 13.8484 | 16.1401 | 13.2678 | 33.0866 | 41.711 | 16.3015 | 13.4005 | 33.4176 | 42.1282
1650 | 113.1788 | 177.6189 | 115.5221 | 180.506 | 5.9809 | 15.2049 | 1650 | 46.4659 | 189.8088 | 48.8492 | 192.9853 | 23.9984 | 16.3631 | 2.7637 | 2.9836 | 9.4382 | 12.2668 | 6.1583 | 7.909 | 18.2507 | 15.7613 | 20.5574 | 17.5448 | 34.5071 | 46.3418 | 20.7762 | 17.7316 | 34.8744 | 46.835
1700 | 140.9831 | 198.4785 | 118.4346 | 154.7116 | 14.4977 | 32.1417 | 1700 | 59.1857 | 214.2527 | 51.661 | 166.5827 | 24.7005 | 34.7334 | 6.1825 | 7.4592 | 9.8042 | 12.1867 | 5.0132 | 7.4882 | 24.0311 | 18.5511 | 22.9752 | 16.5521 | 38.7917 | 58.2621 | 23.235 | 16.7392 | 39.2303 | 58.9208
1750 | 74.6565 | 92.1298 | 76.9314 | 96.1541 | 17.2062 | 28.1026 | 1750 | 32.0522 | 99.8842 | 34.3499 | 103.9442 | 18.1709 | 30.3561 | 1.4978 | 2.3306 | 0.87835 | 0.81693 | 4.054 | 5.2137 | 13.6204 | 9.358 | 15.924 | 10.9055 | 30.3025 | 37.8012 | 16.1149 | 11.0362 | 30.6658 | 38.2543
1800 | 97.575 | 134.9997 | 101.9359 | 143.2481 | 16.0425 | 26.9703 | 1800 | 42.8152 | 147.6372 | 47.1409 | 156.2821 | 20.5754 | 29.4291 | 1.2741 | 1.9338 | 1.2562 | 0.51809 | 4.411 | 5.6881 | 18.7889 | 14.4703 | 22.9969 | 18.0551 | 32.2966 | 42.2105 | 23.2887 | 18.2843 | 32.7065 | 42.7462
1850 | 105.0297 | 143.1978 | 114.3047 | 158.474 | 15.0279 | 25.6634 | 1850 | 47.2599 | 157.5421 | 54.7951 | 174.2509 | 19.6897 | 28.2501 | 3.7003 | 6.0222 | 1.6942 | 2.6965 | 5.2483 | 7.5188 | 21.6378 | 16.6893 | 28.109 | 22.0952 | 31.8709 | 42.1559 | 28.4861 | 22.3916 | 32.2985 | 42.7215
1900 | 113.2284 | 163.0739 | 124.9435 | 183.5766 | 21.2653 | 41.4249 | 1900 | 52.0409 | 181.121 | 62.0148 | 203.6142 | 21.9715 | 45.9898 | 4.3036 | 6.3915 | 2.4847 | 1.8066 | 4.6866 | 7.5184 | 24.4847 | 19.8622 | 33.2534 | 27.8797 | 37.7337 | 59.2233 | 33.7243 | 28.2745 | 38.268 | 60.0619
1950 | 112.7975 | 159.8159 | 170.9234 | 262.729 | 31.3362 | 69.5263 | 1950 | 52.2535 | 177.2359 | 88.2102 | 294.0686 | 26.3145 | 77.8255 | 3.421 | 3.8527 | 3.1582 | 1.8674 | 4.9505 | 9.4754 | 25.0888 | 19.7398 | 49.4925 | 43.6661 | 47.6308 | 88.5093 | 50.2313 | 44.3179 | 48.3418 | 89.8304
2000 | 155.1615 | 258.613 | 144.5215 | 206.5351 | 24.5455 | 32.1179 | 2000 | 74.1108 | 289.4062 | 77.9914 | 232.129 | 17.2993 | 36.2789 | 1.1068 | 2.7707 | 2.2833 | 1.8853 | 2.5301 | 2.9862 | 37.0602 | 34.9026 | 46.2777 | 38.8135 | 32.9118 | 37.2195 | 47.0049 | 39.4233 | 33.4289 | 37.8044