## Clonee 220 kV
Terminal | Clonee 220 kV |  | Terminal | Clonee 220 kV
Terminal Name | Clonee 220 kV |  | Terminal Name | Clonee 220 kV_Corduff 110 kV |  | Clonee 220 kV_Corduff 220 kV |  | Clonee 220 kV_Woodland 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.8217 | 12.9573 | 50 | 3.032 | 2.4835 | 7.617 | 5.7105 | 6.5262 | 7.5388
100 | 21.2812 | 28.631 | 100 | 7.8222 | 6.659 | 19.0673 | 15.1286 | 16.6617 | 18.2105
150 | 39.2144 | 42.3247 | 150 | 17.3847 | 16.2262 | 38.401 | 35.1803 | 35.3857 | 33.8671
200 | 11.1819 | 23.5599 | 200 | 5.4439 | 6.3959 | 10.5336 | 12.4619 | 10.1625 | 7.9176
250 | 20.2095 | 37.6874 | 250 | 5.592 | 4.4961 | 17.1958 | 10.4759 | 11.2073 | 12.9284
300 | 55.6653 | 56.5053 | 300 | 15.9928 | 12.1567 | 54.9383 | 39.3582 | 38.7979 | 31.664
350 | 31.5774 | 48.2058 | 350 | 14.5649 | 5.2636 | 43.4833 | 17.0397 | 22.0148 | 13.1553
400 | 6.4253 | 59.2146 | 400 | 4.9362 | 1.4165 | 13.571 | 4.6193 | 3.5939 | 17.361
450 | 17.6505 | 72.7467 | 450 | 2.146 | 2.259 | 4.6027 | 2.0586 | 7.2068 | 25.9482
500 | 32.0701 | 86.2218 | 500 | 8.5652 | 6.452 | 17.9687 | 9.3992 | 17.01 | 34.5333
550 | 54.1875 | 97.0077 | 550 | 21.402 | 15.6421 | 42.6674 | 25.2278 | 32.8158 | 42.0294
600 | 73.3698 | 87.5173 | 600 | 29.9324 | 24.7741 | 74.0312 | 48.2873 | 47.4508 | 33.5167
650 | 46.3634 | 94.9412 | 650 | 19.933 | 14.6886 | 62.1731 | 26.2069 | 29.6533 | 27.1255
700 | 21.5632 | 110.4555 | 700 | 23.5614 | 9.1866 | 48.6226 | 14.6813 | 17.5321 | 37.4116
750 | 5.9597 | 116.9568 | 750 | 17.213 | 6.7751 | 26.6735 | 11.1592 | 7.4616 | 38.9702
800 | 11.0228 | 129.7233 | 800 | 13.247 | 6.8004 | 18.559 | 8.5839 | 2.4627 | 45.469
850 | 17.5564 | 146.2386 | 850 | 17.3004 | 9.6543 | 12.8167 | 6.6207 | 4.095 | 56.8197
900 | 21.4386 | 148.4015 | 900 | 6.3369 | 6.624 | 9.8549 | 4.8667 | 5.6279 | 55.9049
950 | 26.0993 | 158.1634 | 950 | 9.1638 | 6.816 | 6.5493 | 2.8534 | 8.335 | 58.0577
1000 | 29.9458 | 167.3679 | 1000 | 10.6755 | 9.7856 | 4.2619 | 1.76 | 10.3661 | 61.4808
1050 | 33.2076 | 169.9832 | 1050 | 3.4998 | 6.1753 | 2.3285 | 1.0527 | 11.6191 | 60.4666
1100 | 36.9873 | 187.1185 | 1100 | 0.56013 | 2.4882 | 1.5003 | 0.64024 | 13.7862 | 68.7156
1150 | 40.5018 | 199.5125 | 1150 | 2.8577 | 7.726 | 2.6191 | 1.6551 | 16.603 | 76.9155
1200 | 43.6331 | 207.6298 | 1200 | 3.757 | 14.2387 | 4.1122 | 2.1711 | 17.4478 | 77.4255
1250 | 47.5535 | 230.2093 | 1250 | 0.86567 | 6.7768 | 5.8928 | 3.6333 | 21.0032 | 93.0045
1300 | 51.4674 | 254.5295 | 1300 | 0.92217 | 6.6321 | 7.6309 | 5.0772 | 25.1229 | 112.4686
1350 | 54.8397 | 270.3316 | 1350 | 3.5624 | 6.435 | 9.2067 | 5.8907 | 27.1785 | 120.8009
1400 | 56.5264 | 243.8326 | 1400 | 2.6811 | 3.5719 | 10.4593 | 5.9929 | 27.9826 | 106.626
1450 | 59.2864 | 256.4287 | 1450 | 2.4718 | 2.3871 | 11.8584 | 5.9674 | 24.8708 | 94.7946
1500 | 64.05 | 286.9495 | 1500 | 2.2925 | 3.6142 | 13.981 | 8.4611 | 31.1925 | 122.0009
1550 | 68.3195 | 311.6978 | 1550 | 2.233 | 1.9733 | 16.0637 | 10.6832 | 34.2896 | 134.6509
1600 | 73.9511 | 356.7126 | 1600 | 1.5634 | 1.8889 | 18.6862 | 14.745 | 41.696 | 171.9349
1650 | 78.0335 | 374.0144 | 1650 | 2.6662 | 3.2689 | 20.7455 | 16.8395 | 46.4657 | 189.8063
1700 | 82.4953 | 352.37 | 1700 | 3.4038 | 8.0455 | 23.3202 | 20.0208 | 59.179 | 214.2093
1750 | 76.6836 | 286.4934 | 1750 | 0.97531 | 2.4905 | 21.1833 | 10.1475 | 32.0533 | 99.8902
1800 | 85.2009 | 352.0904 | 1800 | 1.4663 | 2.0773 | 25.2674 | 15.8281 | 42.8147 | 147.6353
1850 | 89.4757 | 361.1734 | 1850 | 0.33332 | 6.5877 | 27.8455 | 18.3613 | 47.2605 | 157.544
1900 | 95.677 | 404.2261 | 1900 | 2.8083 | 7.1494 | 31.1589 | 22.0706 | 52.0409 | 181.121
1950 | 99.0982 | 409.0674 | 1950 | 3.1739 | 4.4031 | 33.2848 | 21.8823 | 52.2542 | 177.2386
2000 | 113.6601 | 544.3387 | 2000 | 1.8441 | 2.986 | 41.3354 | 39.0402 | 74.1106 | 289.4046

## Corduff 110 kV
Terminal | Corduff 110 kV |  | Terminal | Corduff 110 kV
Terminal Name | Corduff 110 kV |  | Terminal Name | Corduff 110 kV_Clonee 220 kV |  | Corduff 110 kV_Corduff 220 kV |  | Corduff 110 kV_Woodland 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 3.5832 | 3.6526 | 50 | 3.032 | 2.4835 | 3.1931 | 3.4411 | 2.6333 | 2.4964
100 | 7.8293 | 8.0084 | 100 | 7.8222 | 6.659 | 8.1778 | 8.7914 | 6.9884 | 6.7288
150 | 11.1395 | 11.4656 | 150 | 17.3847 | 16.2262 | 17.8174 | 18.8584 | 16.5444 | 16.4558
200 | 7.2805 | 7.5334 | 200 | 5.4439 | 6.3959 | 5.3121 | 5.4517 | 6.079 | 6.481
250 | 11.226 | 11.3213 | 250 | 5.592 | 4.4961 | 6.1787 | 7.7586 | 4.5202 | 4.5475
300 | 17.3227 | 18.5604 | 300 | 15.9928 | 12.1567 | 17.7846 | 26.5595 | 12.1838 | 12.6528
350 | 14.7628 | 13.4687 | 350 | 14.5649 | 5.2636 | 16.9631 | 16.0684 | 9.2739 | 5.4763
400 | 19.5198 | 19.7488 | 400 | 4.9362 | 1.4165 | 5.9161 | 5.3581 | 2.6023 | 1.4686
450 | 26.583 | 26.5904 | 450 | 2.146 | 2.259 | 2.1141 | 2.1149 | 2.2466 | 2.2873
500 | 35.2744 | 35.4088 | 500 | 8.5652 | 6.452 | 9.168 | 9.5633 | 7.2154 | 6.5522
550 | 42.0548 | 42.8713 | 550 | 21.402 | 15.6421 | 23.1673 | 25.837 | 17.2522 | 15.8737
600 | 32.468 | 32.097 | 600 | 29.9324 | 24.7741 | 32.5585 | 43.0117 | 24.6107 | 25.2333
650 | 41.0946 | 39.0915 | 650 | 19.933 | 14.6886 | 22.3174 | 24.8746 | 15.5149 | 14.8134
700 | 38.0489 | 39.2789 | 700 | 23.5614 | 9.1866 | 26.9416 | 23.6116 | 15.2309 | 9.4028
750 | 60.8289 | 61.7416 | 750 | 17.213 | 6.7751 | 19.7503 | 18.4665 | 10.863 | 6.9536
800 | 75.7315 | 76.0525 | 800 | 13.247 | 6.8004 | 14.7607 | 14.2998 | 9.4108 | 6.9154
850 | 150.5217 | 150.973 | 850 | 17.3004 | 9.6543 | 19.0212 | 18.7718 | 13.0046 | 9.8415
900 | 89.2558 | 89.1406 | 900 | 6.3369 | 6.624 | 8.2973 | 7.864 | 3.763 | 6.6702
950 | 181.5516 | 181.6282 | 950 | 9.1638 | 6.816 | 9.7764 | 9.7567 | 7.9326 | 7.0271
1000 | 339.29 | 339.0929 | 1000 | 10.6755 | 9.7856 | 11.1888 | 11.1245 | 9.7957 | 9.8944
1050 | 173.3876 | 173.3859 | 1050 | 3.4998 | 6.1753 | 2.9235 | 2.9204 | 5.144 | 6.1677
1100 | 115.2732 | 115.3469 | 1100 | 0.56013 | 2.4882 | 1.1832 | 1.1846 | 1.4732 | 2.5932
1150 | 86.0502 | 85.8806 | 1150 | 2.8577 | 7.726 | 1.7362 | 1.7072 | 5.5776 | 7.4684
1200 | 77.7756 | 78.5626 | 1200 | 3.757 | 14.2387 | 1.9538 | 1.9484 | 10.0252 | 13.7512
1250 | 69.0219 | 68.7957 | 1250 | 0.86567 | 6.7768 | 1.8896 | 1.9684 | 3.9485 | 6.5238
1300 | 55.7941 | 55.6323 | 1300 | 0.92217 | 6.6321 | 2.0215 | 2.1144 | 3.4915 | 6.4059
1350 | 53.3607 | 53.3263 | 1350 | 3.5624 | 6.435 | 2.9266 | 2.8708 | 4.966 | 6.2002
1400 | 46.6118 | 46.6407 | 1400 | 2.6811 | 3.5719 | 2.6088 | 2.5689 | 3.3553 | 3.4193
1450 | 40.5661 | 40.5684 | 1450 | 2.4718 | 2.3871 | 2.5325 | 2.5325 | 2.2696 | 2.2528
1500 | 36.8072 | 36.8256 | 1500 | 2.2925 | 3.6142 | 2.418 | 2.4137 | 2.8083 | 3.4073
1550 | 32.9375 | 32.9398 | 1550 | 2.233 | 1.9733 | 2.3687 | 2.3652 | 1.9382 | 1.8926
1600 | 29.8396 | 29.8126 | 1600 | 1.5634 | 1.8889 | 2.0923 | 2.1307 | 0.48611 | 1.6835
1650 | 28.6911 | 28.7008 | 1650 | 2.6662 | 3.2689 | 2.5352 | 2.4731 | 2.7622 | 2.9811
1700 | 27.0353 | 27.1752 | 1700 | 3.4038 | 8.0455 | 2.6067 | 2.1815 | 6.174 | 7.4464
1750 | 24.8755 | 24.8204 | 1750 | 0.97531 | 2.4905 | 1.8176 | 1.998 | 1.496 | 2.3278
1800 | 23.1497 | 23.1247 | 1800 | 1.4663 | 2.0773 | 1.9691 | 2.0244 | 1.276 | 1.9362
1850 | 22.1038 | 21.9642 | 1850 | 0.33332 | 6.5877 | 1.3129 | 1.6261 | 3.7014 | 6.0243
1900 | 20.4173 | 20.4895 | 1900 | 2.8083 | 7.1494 | 2.4471 | 2.5138 | 4.3035 | 6.3912
1950 | 19.9603 | 19.9597 | 1950 | 3.1739 | 4.4031 | 2.8372 | 2.727 | 3.4193 | 3.85
2000 | 20.1686 | 20.1296 | 2000 | 1.8441 | 2.986 | 2.2688 | 2.2846 | 1.1076 | 2.7716

## Corduff 220 kV
Terminal | Corduff 220 kV |  | Terminal | Corduff 220 kV
Terminal Name | Corduff 220 kV |  | Terminal Name | Corduff 220 kV_Clonee 220 kV |  | Corduff 220 kV_Corduff 110 kV |  | Corduff 220 kV_Woodland 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.1779 | 9.0457 | 50 | 7.617 | 5.7105 | 3.1931 | 3.4411 | 6.2255 | 5.7526
100 | 20.2787 | 22.3824 | 100 | 19.0673 | 15.1286 | 8.1778 | 8.7914 | 16.1803 | 15.3128
150 | 39.7371 | 43.1272 | 150 | 38.401 | 35.1803 | 17.8174 | 18.8584 | 35.7282 | 35.6883
200 | 11.1919 | 13.9875 | 200 | 10.5336 | 12.4619 | 5.3121 | 5.4517 | 11.1326 | 12.582
250 | 19.9812 | 26.0315 | 250 | 17.1958 | 10.4759 | 6.1787 | 7.7586 | 11.3971 | 10.6409
300 | 61.6037 | 92.5099 | 300 | 54.9383 | 39.3582 | 17.7846 | 26.5595 | 40.3225 | 41.0185
350 | 50.5811 | 48.6426 | 350 | 43.4833 | 17.0397 | 16.9631 | 16.0684 | 28.1548 | 17.6698
400 | 15.9459 | 14.7798 | 400 | 13.571 | 4.6193 | 5.9161 | 5.3581 | 7.8034 | 4.7707
450 | 5.2713 | 5.3623 | 450 | 4.6027 | 2.0586 | 2.1141 | 2.1149 | 2.9963 | 2.1259
500 | 20.281 | 21.6687 | 500 | 17.9687 | 9.3992 | 9.168 | 9.5633 | 12.45 | 9.6649
550 | 47.9587 | 55.5832 | 550 | 42.6674 | 25.2278 | 23.1673 | 25.837 | 30.2495 | 25.8282
600 | 84.1559 | 114.3554 | 600 | 74.0312 | 48.2873 | 32.5585 | 43.0117 | 51.2915 | 49.3769
650 | 72.0937 | 73.0063 | 650 | 62.1731 | 26.2069 | 22.3174 | 24.8746 | 39.0023 | 26.6535
700 | 56.4982 | 48.3793 | 700 | 48.6226 | 14.6813 | 26.9416 | 23.6116 | 29.008 | 15.133
750 | 30.3927 | 28.565 | 750 | 26.6735 | 11.1592 | 19.7503 | 18.4665 | 17.3497 | 11.3962
800 | 20.9169 | 20.2196 | 800 | 18.559 | 8.5839 | 14.7607 | 14.2998 | 12.6019 | 8.735
850 | 14.2069 | 13.988 | 850 | 12.8167 | 6.6207 | 19.0212 | 18.7718 | 9.2754 | 6.7121
900 | 11.1157 | 11.0294 | 900 | 9.8549 | 4.8667 | 8.2973 | 7.864 | 6.9822 | 4.9139
950 | 7.4246 | 7.3502 | 950 | 6.5493 | 2.8534 | 9.7764 | 9.7567 | 4.2674 | 2.8662
1000 | 4.8517 | 4.8228 | 1000 | 4.2619 | 1.76 | 11.1888 | 11.1245 | 2.7097 | 1.7738
1050 | 2.6357 | 2.6321 | 1050 | 2.3285 | 1.0527 | 2.9235 | 2.9204 | 1.5227 | 1.0567
1100 | 1.6997 | 1.7016 | 1100 | 1.5003 | 0.64024 | 1.1832 | 1.1846 | 0.95335 | 0.63631
1150 | 2.8243 | 2.8286 | 1150 | 2.6191 | 1.6551 | 1.7362 | 1.7072 | 2.028 | 1.6341
1200 | 4.5457 | 4.5628 | 1200 | 4.1122 | 2.1711 | 1.9538 | 1.9484 | 2.8459 | 2.1292
1250 | 6.3564 | 6.3723 | 1250 | 5.8928 | 3.6333 | 1.8896 | 1.9684 | 4.4473 | 3.5472
1300 | 8.1079 | 8.1174 | 1300 | 7.6309 | 5.0772 | 2.0215 | 2.1144 | 6.0854 | 4.9348
1350 | 9.8124 | 9.8294 | 1350 | 9.2067 | 5.8907 | 2.9266 | 2.8708 | 7.1768 | 5.699
1400 | 11.4011 | 11.4398 | 1400 | 10.4593 | 5.9929 | 2.6088 | 2.5689 | 8.1577 | 5.7636
1450 | 13.1245 | 13.2361 | 1450 | 11.8584 | 5.9674 | 2.5325 | 2.5325 | 7.856 | 5.7213
1500 | 14.9954 | 15.0286 | 1500 | 13.981 | 8.4611 | 2.418 | 2.4137 | 10.4871 | 8.0517
1550 | 16.9666 | 16.9577 | 1550 | 16.0637 | 10.6832 | 2.3687 | 2.3652 | 12.4329 | 10.1211
1600 | 19.138 | 19.0012 | 1600 | 18.6862 | 14.745 | 2.0923 | 2.1307 | 15.8694 | 13.8507
1650 | 21.0881 | 20.8121 | 1650 | 20.7455 | 16.8395 | 2.5352 | 2.4731 | 18.2507 | 15.7613
1700 | 23.1058 | 22.1366 | 1700 | 23.3202 | 20.0208 | 2.6067 | 2.1815 | 24.0287 | 18.5481
1750 | 23.7475 | 24.0815 | 1750 | 21.1833 | 10.1475 | 1.8176 | 1.998 | 13.6207 | 9.3583
1800 | 26.8278 | 26.7318 | 1800 | 25.2674 | 15.8281 | 1.9691 | 2.0244 | 18.7887 | 14.4701
1850 | 29.3182 | 29.0464 | 1850 | 27.8455 | 18.3613 | 1.3129 | 1.6261 | 21.6382 | 16.6898
1900 | 32.2935 | 31.8542 | 1900 | 31.1589 | 22.0706 | 2.4471 | 2.5138 | 24.4847 | 19.8622
1950 | 34.8159 | 34.4517 | 1950 | 33.2848 | 21.8823 | 2.8372 | 2.727 | 25.0892 | 19.7402
2000 | 40.5148 | 39.3336 | 2000 | 41.3354 | 39.0402 | 2.2688 | 2.2846 | 37.0601 | 34.9025

## Woodland 220 kV
Terminal | Woodland 220 kV |  | Terminal | Woodland 220 kV
Terminal Name | Woodland 220 kV |  | Terminal Name | Woodland 220 kV_Clonee 220 kV |  | Woodland 220 kV_Corduff 110 kV |  | Woodland 220 kV_Corduff 220 kV
Study Case | step0 |  | Study Case | step0 |  | step0 |  | step0
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | Full Result Name | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1 | step0_Base_Case | step0_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 7.3678 | 7.613 | 50 | 6.5262 | 7.5388 | 2.6333 | 2.4964 | 6.2255 | 5.7526
100 | 18.1523 | 18.4732 | 100 | 16.6617 | 18.2105 | 6.9884 | 6.7288 | 16.1803 | 15.3128
150 | 35.1892 | 34.3974 | 150 | 35.3857 | 33.8671 | 16.5444 | 16.4558 | 35.7282 | 35.6883
200 | 8.6121 | 8.0828 | 200 | 10.1625 | 7.9176 | 6.079 | 6.481 | 11.1326 | 12.582
250 | 12.8662 | 13.4798 | 250 | 11.2073 | 12.9284 | 4.5202 | 4.5475 | 11.3971 | 10.6409
300 | 36.8096 | 32.9328 | 300 | 38.7979 | 31.664 | 12.1838 | 12.6528 | 40.3225 | 41.0185
350 | 9.4145 | 13.5904 | 350 | 22.0148 | 13.1553 | 9.2739 | 5.4763 | 28.1548 | 17.6698
400 | 11.468 | 17.9021 | 400 | 3.5939 | 17.361 | 2.6023 | 1.4686 | 7.8034 | 4.7707
450 | 20.2363 | 26.7642 | 450 | 7.2068 | 25.9482 | 2.2466 | 2.2873 | 2.9963 | 2.1259
500 | 29.7132 | 35.5495 | 500 | 17.01 | 34.5333 | 7.2154 | 6.5522 | 12.45 | 9.6649
550 | 40.8815 | 43.0817 | 550 | 32.8158 | 42.0294 | 17.2522 | 15.8737 | 30.2495 | 25.8282
600 | 40.9982 | 34.367 | 600 | 47.4508 | 33.5167 | 24.6107 | 25.2333 | 51.2915 | 49.3769
650 | 16.8485 | 27.7395 | 650 | 29.6533 | 27.1255 | 15.5149 | 14.8134 | 39.0023 | 26.6535
700 | 17.5483 | 38.1266 | 700 | 17.5321 | 37.4116 | 15.2309 | 9.4028 | 29.008 | 15.133
750 | 22.5653 | 39.6915 | 750 | 7.4616 | 38.9702 | 10.863 | 6.9536 | 17.3497 | 11.3962
800 | 28.0995 | 46.2529 | 800 | 2.4627 | 45.469 | 9.4108 | 6.9154 | 12.6019 | 8.735
850 | 35.5654 | 57.557 | 850 | 4.095 | 56.8197 | 13.0046 | 9.8415 | 9.2754 | 6.7121
900 | 37.4509 | 56.3685 | 900 | 5.6279 | 55.9049 | 3.763 | 6.6702 | 6.9822 | 4.9139
950 | 39.8016 | 58.2952 | 950 | 8.335 | 58.0577 | 7.9326 | 7.0271 | 4.2674 | 2.8662
1000 | 42.7478 | 61.5031 | 1000 | 10.3661 | 61.4808 | 9.7957 | 9.8944 | 2.7097 | 1.7738
1050 | 43.7703 | 60.3197 | 1050 | 11.6191 | 60.4666 | 5.144 | 6.1677 | 1.5227 | 1.0567
1100 | 48.2564 | 68.2541 | 1100 | 13.7862 | 68.7156 | 1.4732 | 2.5932 | 0.95335 | 0.63631
1150 | 54.1637 | 75.9457 | 1150 | 16.603 | 76.9155 | 5.5776 | 7.4684 | 2.028 | 1.6341
1200 | 54.3541 | 75.9905 | 1200 | 17.4478 | 77.4255 | 10.0252 | 13.7512 | 2.8459 | 2.1292
1250 | 62.6508 | 90.9386 | 1250 | 21.0032 | 93.0045 | 3.9485 | 6.5238 | 4.4473 | 3.5472
1300 | 72.6071 | 109.338 | 1300 | 25.1229 | 112.4686 | 3.4915 | 6.4059 | 6.0854 | 4.9348
1350 | 76.7264 | 116.8493 | 1350 | 27.1785 | 120.8009 | 4.966 | 6.2002 | 7.1768 | 5.699
1400 | 76.6149 | 102.4987 | 1400 | 27.9826 | 106.626 | 3.3553 | 3.4193 | 8.1577 | 5.7636
1450 | 66.4472 | 90.8176 | 1450 | 24.8708 | 94.7946 | 2.2696 | 2.2528 | 7.856 | 5.7213
1500 | 81.2057 | 116.0034 | 1500 | 31.1925 | 122.0009 | 2.8083 | 3.4073 | 10.4871 | 8.0517
1550 | 86.956 | 127.7385 | 1550 | 34.2896 | 134.6509 | 1.9382 | 1.8926 | 12.4329 | 10.1211
1600 | 103.1195 | 161.6476 | 1600 | 41.696 | 171.9349 | 0.48611 | 1.6835 | 15.8694 | 13.8507
1650 | 113.1779 | 177.6165 | 1650 | 46.4657 | 189.8063 | 2.7622 | 2.9811 | 18.2507 | 15.7613
1700 | 140.966 | 198.438 | 1700 | 59.179 | 214.2093 | 6.174 | 7.4464 | 24.0287 | 18.5481
1750 | 74.6598 | 92.1355 | 1750 | 32.0533 | 99.8902 | 1.496 | 2.3278 | 13.6207 | 9.3583
1800 | 97.5738 | 134.9977 | 1800 | 42.8147 | 147.6353 | 1.276 | 1.9362 | 18.7887 | 14.4701
1850 | 105.0309 | 143.1998 | 1850 | 47.2605 | 157.544 | 3.7014 | 6.0243 | 21.6382 | 16.6898
1900 | 113.2283 | 163.0739 | 1900 | 52.0409 | 181.121 | 4.3035 | 6.3912 | 24.4847 | 19.8622
1950 | 112.7991 | 159.8184 | 1950 | 52.2542 | 177.2386 | 3.4193 | 3.85 | 25.0892 | 19.7402
2000 | 155.161 | 258.6115 | 2000 | 74.1106 | 289.4046 | 1.1076 | 2.7716 | 37.0601 | 34.9025