## Clonee 220 kV
Terminal | Clonee 220 kV |  | Terminal | Clonee 220 kV
Terminal Name | Clonee 220 kV |  | Terminal Name | Clonee 220 kV_Corduff 110 kV |  | Clonee 220 kV_Corduff 220 kV |  | Clonee 220 kV_Cruiserath 220 kV |  | Clonee 220 kV_Woodland 220 kV
Study Case | step1 |  | Study Case | step1 |  | step1 |  | step1 |  | step1
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.8266 | 12.9636 | 50 | 3.0414 | 2.4671 | 7.6243 | 5.7421 | 7.6244 | 5.7421 | 6.5241 | 7.5443
100 | 21.7149 | 28.9943 | 100 | 8.0847 | 6.8427 | 19.5264 | 15.6566 | 19.5271 | 15.6572 | 17.0574 | 18.5897
150 | 37.7278 | 39.3605 | 150 | 17.4178 | 16.2966 | 37.4508 | 35.2126 | 37.4541 | 35.2157 | 34.6762 | 32.5685
200 | 10.2973 | 24.0691 | 200 | 4.6744 | 5.6941 | 8.9706 | 10.7407 | 8.972 | 10.7424 | 8.3287 | 6.7536
250 | 20.6449 | 38.8471 | 250 | 4.962 | 3.6517 | 16.8309 | 8.7853 | 16.835 | 8.7874 | 10.6326 | 13.6816
300 | 61.5095 | 54.0452 | 300 | 19.5749 | 15.1571 | 62.4705 | 47.0054 | 62.4924 | 47.022 | 43.9273 | 31.5845
350 | 28.6657 | 48.5146 | 350 | 14.8171 | 4.9543 | 40.8228 | 15.4155 | 40.8423 | 15.4228 | 20.0712 | 13.3517
400 | 6.265 | 59.8822 | 400 | 5.2993 | 1.6 | 13.0906 | 4.5794 | 13.0988 | 4.5822 | 3.4144 | 18.0235
450 | 17.6517 | 72.709 | 450 | 2.5106 | 2.6792 | 4.6372 | 2.0693 | 4.6409 | 2.0709 | 7.2033 | 25.9175
500 | 32.6099 | 86.1612 | 500 | 10.9249 | 8.2588 | 18.7776 | 9.8674 | 18.7959 | 9.877 | 17.4132 | 34.5275
550 | 53.6427 | 94.2817 | 550 | 26.9125 | 19.9452 | 43.7573 | 26.666 | 43.8088 | 26.6974 | 32.723 | 40.1467
600 | 60.3807 | 85.389 | 600 | 28.1298 | 24.4824 | 62.0802 | 36.7019 | 62.1672 | 36.7533 | 36.2712 | 26.7232
650 | 53.7594 | 99.4481 | 650 | 43.1099 | 16.6291 | 77.3026 | 20.0106 | 77.4296 | 20.0435 | 32.6965 | 31.5614
700 | 12.1037 | 111.0437 | 700 | 27.3467 | 14.2619 | 35.3139 | 12.8724 | 35.3812 | 12.897 | 12.2156 | 38.675
750 | 11.6777 | 117.0461 | 750 | 31.7826 | 12.1608 | 22.3251 | 8.213 | 22.3739 | 8.2309 | 5.9959 | 38.6051
800 | 14.5362 | 130.443 | 800 | 31.3284 | 16.7875 | 18.0474 | 8.0008 | 18.0923 | 8.0208 | 5.1347 | 46.2518
850 | 15.8965 | 145.8784 | 850 | 9.2074 | 5.0635 | 14.7127 | 7.5793 | 14.7541 | 7.6006 | 3.1559 | 56.3985
900 | 21.626 | 151.0751 | 900 | 6.488 | 8.9356 | 9.9399 | 3.9782 | 9.9712 | 3.9907 | 6.4973 | 58.4914
950 | 25.8323 | 159.1417 | 950 | 3.6974 | 3.4276 | 6.8738 | 2.9618 | 6.8979 | 2.9722 | 8.3235 | 59.2481
1000 | 29.9055 | 167.8725 | 1000 | 1.4852 | 1.7025 | 4.2477 | 1.7755 | 4.2643 | 1.7824 | 10.6186 | 62.669
1050 | 33.0866 | 166.3517 | 1050 | 0.96487 | 2.4829 | 2.3216 | 1.2835 | 2.3316 | 1.289 | 11.3092 | 57.4301
1100 | 36.7972 | 184.801 | 1100 | 0.58646 | 2.1457 | 1.7982 | 1.6575 | 1.8067 | 1.6653 | 13.6994 | 67.5092
1150 | 39.9529 | 190.5987 | 1150 | 0.35573 | 0.6436 | 2.573 | 1.5116 | 2.5863 | 1.5194 | 15.4014 | 70.0137
1200 | 43.0586 | 197.5449 | 1200 | 0.27797 | 1.5998 | 4.06 | 1.6719 | 4.0828 | 1.6813 | 15.527 | 66.986
1250 | 47.3072 | 224.2376 | 1250 | 0.051757 | 0.86079 | 5.9547 | 3.1155 | 5.9909 | 3.1345 | 19.9365 | 86.9079
1300 | 51.4419 | 248.5874 | 1300 | 0.41777 | 1.8294 | 7.9019 | 4.7465 | 7.9539 | 4.7777 | 24.2587 | 106.1212
1350 | 55.3873 | 266.8725 | 1350 | 1.4162 | 2.7616 | 9.9193 | 6.4354 | 9.9898 | 6.4812 | 27.2763 | 117.0184
1400 | 57.7116 | 252.0251 | 1400 | 3.3867 | 3.8062 | 11.5589 | 7.0496 | 11.6473 | 7.1035 | 28.9276 | 111.0499
1450 | 60.1222 | 255.177 | 1450 | 5.44 | 2.4732 | 12.8832 | 6.7008 | 12.9889 | 6.7558 | 25.3451 | 93.3798
1500 | 64.9291 | 284.499 | 1500 | 5.3297 | 10.3296 | 15.2114 | 9.3129 | 15.345 | 9.3947 | 31.0376 | 117.0218
1550 | 70.0871 | 316.2454 | 1550 | 5.3935 | 11.2764 | 17.9305 | 11.9836 | 18.0988 | 12.096 | 35.9775 | 138.7185
1600 | 74.7155 | 349.9996 | 1600 | 10.2823 | 22.0289 | 20.1033 | 14.0576 | 20.3044 | 14.1982 | 41.0502 | 164.9185
1650 | 80.6975 | 377.023 | 1650 | 6.5982 | 13.4496 | 23.58 | 18.7381 | 23.831 | 18.9376 | 48.8478 | 192.9807
1700 | 81.0899 | 312.9488 | 1700 | 4.2667 | 13.2368 | 24.9799 | 17.8189 | 25.2623 | 18.0204 | 51.6532 | 166.5576
1750 | 80.4867 | 293.8445 | 1750 | 2.0002 | 1.0248 | 25.2729 | 11.78 | 25.5759 | 11.9212 | 34.3509 | 103.9499
1800 | 91.2171 | 368.4994 | 1800 | 3.3675 | 0.5684 | 31.191 | 19.6836 | 31.5869 | 19.9334 | 47.1397 | 156.2721
1850 | 97.4618 | 382.0739 | 1850 | 2.8987 | 3.0546 | 35.6423 | 24.2677 | 36.1205 | 24.5933 | 54.7841 | 174.2118
1900 | 106.687 | 435.2251 | 1900 | 4.1823 | 1.9821 | 41.6282 | 30.9132 | 42.2177 | 31.351 | 62.0172 | 203.6243
1950 | 121.7734 | 507.2377 | 1950 | 4.0522 | 2.1017 | 52.068 | 48.8628 | 52.8452 | 49.5921 | 88.2134 | 294.0785
2000 | 123.961 | 469.6432 | 2000 | 3.4462 | 2.1438 | 55.4247 | 43.6077 | 56.2956 | 44.2929 | 77.9919 | 232.1325

## Corduff 110 kV
Terminal | Corduff 110 kV |  | Terminal | Corduff 110 kV
Terminal Name | Corduff 110 kV |  | Terminal Name | Corduff 110 kV_Clonee 220 kV |  | Corduff 110 kV_Corduff 220 kV |  | Corduff 110 kV_Cruiserath 220 kV |  | Corduff 110 kV_Woodland 220 kV
Study Case | step1 |  | Study Case | step1 |  | step1 |  | step1 |  | step1
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 3.5961 | 3.6374 | 50 | 3.0414 | 2.4671 | 3.2038 | 3.4224 | 3.2039 | 3.4225 | 2.6391 | 2.4797
100 | 7.992 | 8.1057 | 100 | 8.0847 | 6.8427 | 8.4502 | 9.0208 | 8.4506 | 9.0211 | 7.2264 | 6.913
150 | 10.5193 | 10.6796 | 150 | 17.4178 | 16.2966 | 17.8155 | 18.7354 | 17.8171 | 18.737 | 16.6621 | 16.5193
200 | 7.5675 | 7.8098 | 200 | 4.6744 | 5.6941 | 4.5316 | 4.6542 | 4.5323 | 4.6549 | 5.3575 | 5.7616
250 | 11.9291 | 12.0984 | 250 | 4.962 | 3.6517 | 5.6064 | 7.1782 | 5.6078 | 7.18 | 3.7729 | 3.6933
300 | 18.472 | 18.9878 | 300 | 19.5749 | 15.1571 | 21.687 | 32.1744 | 21.6946 | 32.1857 | 15.0595 | 15.7653
350 | 15.4996 | 14.5884 | 350 | 14.8171 | 4.9543 | 17.3201 | 15.7066 | 17.3284 | 15.7141 | 9.2889 | 5.1578
400 | 21.541 | 21.9405 | 400 | 5.2993 | 1.6 | 6.3359 | 5.6156 | 6.3398 | 5.6191 | 2.8618 | 1.6532
450 | 30.8393 | 30.8646 | 450 | 2.5106 | 2.6792 | 2.46 | 2.4244 | 2.462 | 2.4263 | 2.6646 | 2.7121
500 | 43.4637 | 43.5681 | 500 | 10.9249 | 8.2588 | 11.6715 | 12.0112 | 11.6829 | 12.0228 | 9.2829 | 8.3889
550 | 47.8148 | 48.6184 | 550 | 26.9125 | 19.9452 | 29.0283 | 32.2435 | 29.0624 | 32.2815 | 21.9899 | 20.2261
600 | 40.7463 | 39.1483 | 600 | 28.1298 | 24.4824 | 30.7118 | 41.7272 | 30.7548 | 41.7856 | 23.7436 | 24.867
650 | 30.1881 | 34.4444 | 650 | 43.1099 | 16.6291 | 49.3558 | 40.9884 | 49.4369 | 41.0557 | 27.7139 | 17.0245
700 | 60.9697 | 63.0459 | 700 | 27.3467 | 14.2619 | 30.5928 | 28.168 | 30.6511 | 28.2217 | 19.7141 | 14.4684
750 | 126.0435 | 130.3505 | 750 | 31.7826 | 12.1608 | 36.5959 | 34.0501 | 36.6759 | 34.1245 | 19.7467 | 12.5029
800 | 192.6552 | 194.4581 | 800 | 31.3284 | 16.7875 | 34.6937 | 33.0881 | 34.7801 | 33.1705 | 22.8063 | 17.0607
850 | 84.8174 | 84.5957 | 850 | 9.2074 | 5.0635 | 10.1351 | 9.7229 | 10.1636 | 9.7502 | 6.9386 | 5.164
900 | 88.2123 | 87.5957 | 900 | 6.488 | 8.9356 | 7.4796 | 6.9518 | 7.5032 | 6.9737 | 6.4517 | 9.0156
950 | 74.5118 | 74.3837 | 950 | 3.6974 | 3.4276 | 3.7844 | 3.7021 | 3.7977 | 3.7151 | 3.682 | 3.5352
1000 | 48.173 | 48.1228 | 1000 | 1.4852 | 1.7025 | 1.5447 | 1.5004 | 1.5507 | 1.5063 | 1.4888 | 1.6826
1050 | 33.363 | 33.3537 | 1050 | 0.96487 | 2.4829 | 0.56291 | 0.55856 | 0.56532 | 0.56095 | 1.9613 | 2.4557
1100 | 26.9359 | 26.9101 | 1100 | 0.58646 | 2.1457 | 0.34895 | 0.34531 | 0.3506 | 0.34693 | 1.4754 | 2.047
1150 | 19.3745 | 19.3731 | 1150 | 0.35573 | 0.6436 | 0.29702 | 0.28903 | 0.29855 | 0.29052 | 0.5562 | 0.64144
1200 | 13.9547 | 13.9501 | 1200 | 0.27797 | 1.5998 | 0.27475 | 0.28528 | 0.27629 | 0.28688 | 1.1156 | 1.5716
1250 | 7.314 | 7.312 | 1250 | 0.051757 | 0.86079 | 0.18789 | 0.19582 | 0.18903 | 0.19701 | 0.51905 | 0.83748
1300 | 4.9302 | 4.9195 | 1300 | 0.41777 | 1.8294 | 0.24404 | 0.24118 | 0.24565 | 0.24277 | 1.1679 | 1.7724
1350 | 17.8054 | 17.8112 | 1350 | 1.4162 | 2.7616 | 1.1171 | 1.0727 | 1.125 | 1.0803 | 2.1039 | 2.6699
1400 | 51.248 | 51.2279 | 1400 | 3.3867 | 3.8062 | 3.2745 | 3.1681 | 3.2995 | 3.1923 | 3.7632 | 3.6974
1450 | 99.6839 | 99.5364 | 1450 | 5.44 | 2.4732 | 6.7111 | 6.7272 | 6.7661 | 6.7824 | 2.2132 | 2.313
1500 | 57.5377 | 57.7161 | 1500 | 5.3297 | 10.3296 | 4.5861 | 4.4501 | 4.6263 | 4.4892 | 7.4673 | 9.6831
1550 | 35.9855 | 35.9353 | 1550 | 5.3935 | 11.2764 | 4.0711 | 3.8316 | 4.1093 | 3.8675 | 7.9392 | 10.3461
1600 | 62.7533 | 62.3481 | 1600 | 10.2823 | 22.0289 | 7.8206 | 7.3249 | 7.8988 | 7.3982 | 15.0147 | 20.0832
1650 | 48.5669 | 48.8402 | 1650 | 6.5982 | 13.4496 | 5.4485 | 5.0258 | 5.5065 | 5.0793 | 9.4383 | 12.2668
1700 | 32.8262 | 32.973 | 1700 | 4.2667 | 13.2368 | 2.8754 | 2.3001 | 2.9079 | 2.3261 | 9.7836 | 12.1592
1750 | 29.0821 | 29.0739 | 1750 | 2.0002 | 1.0248 | 2.5988 | 2.6751 | 2.63 | 2.7072 | 0.88885 | 0.83531
1800 | 37.6735 | 37.6522 | 1800 | 3.3675 | 0.5684 | 4.0774 | 4.0805 | 4.1292 | 4.1323 | 1.241 | 0.50492
1850 | 34.7241 | 34.6854 | 1850 | 2.8987 | 3.0546 | 3.841 | 3.8822 | 3.8925 | 3.9342 | 1.7282 | 2.7178
1900 | 32.5517 | 32.5603 | 1900 | 4.1823 | 1.9821 | 4.6291 | 4.5619 | 4.6946 | 4.6265 | 2.4883 | 1.8158
1950 | 25.935 | 25.9572 | 1950 | 4.0522 | 2.1017 | 4.2155 | 3.9795 | 4.2784 | 4.0389 | 3.1573 | 1.8658
2000 | 20.6412 | 20.656 | 2000 | 3.4462 | 2.1438 | 3.6733 | 3.5999 | 3.731 | 3.6564 | 2.2843 | 1.8859

## Corduff 220 kV
Terminal | Corduff 220 kV |  | Terminal | Corduff 220 kV
Terminal Name | Corduff 220 kV |  | Terminal Name | Corduff 220 kV_Clonee 220 kV |  | Corduff 220 kV_Corduff 110 kV |  | Corduff 220 kV_Cruiserath 220 kV |  | Corduff 220 kV_Woodland 220 kV
Study Case | step1 |  | Study Case | step1 |  | step1 |  | step1 |  | step1
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.1879 | 9.1213 | 50 | 7.6243 | 5.7421 | 3.2038 | 3.4224 | 8.188 | 9.1214 | 6.2256 | 5.7842
100 | 20.7556 | 23.1001 | 100 | 19.5264 | 15.6566 | 8.4502 | 9.0208 | 20.7565 | 23.1011 | 16.5952 | 15.8434
150 | 38.6127 | 42.1926 | 150 | 37.4508 | 35.2126 | 17.8155 | 18.7354 | 38.6161 | 42.1964 | 35.2168 | 35.6968
200 | 9.8824 | 13.0489 | 200 | 8.9706 | 10.7407 | 4.5316 | 4.6542 | 9.8839 | 13.051 | 9.2526 | 10.8169
250 | 19.8246 | 26.4909 | 250 | 16.8309 | 8.7853 | 5.6064 | 7.1782 | 19.8294 | 26.4974 | 10.3205 | 8.9904
300 | 69.7959 | 106.7213 | 300 | 62.4705 | 47.0054 | 21.687 | 32.1744 | 69.8204 | 106.7588 | 46.4223 | 48.9389
350 | 47.6271 | 44.8331 | 350 | 40.8228 | 15.4155 | 17.3201 | 15.7066 | 47.6498 | 44.8545 | 26.1587 | 15.9818
400 | 15.3169 | 14.1915 | 400 | 13.0906 | 4.5794 | 6.3359 | 5.6156 | 15.3265 | 14.2003 | 7.689 | 4.7282
450 | 5.3139 | 5.4253 | 450 | 4.6372 | 2.0693 | 2.46 | 2.4244 | 5.3181 | 5.4295 | 3.0131 | 2.1379
500 | 21.2005 | 22.8248 | 500 | 18.7776 | 9.8674 | 11.6715 | 12.0112 | 21.2212 | 22.847 | 13.0137 | 10.1454
550 | 49.2661 | 58.6137 | 550 | 43.7573 | 26.666 | 29.0283 | 32.2435 | 49.3241 | 58.6827 | 31.0468 | 27.3164
600 | 71.9156 | 99.3595 | 600 | 62.0802 | 36.7019 | 30.7118 | 41.7272 | 72.0163 | 99.4986 | 40.4843 | 37.5256
650 | 90.8431 | 73.6445 | 650 | 77.3026 | 20.0106 | 49.3558 | 40.9884 | 90.9924 | 73.7655 | 43.7259 | 20.672
700 | 40.5709 | 36.9652 | 700 | 35.3139 | 12.8724 | 30.5928 | 28.168 | 40.6482 | 37.0356 | 22.219 | 13.197
750 | 25.8279 | 24.5625 | 750 | 22.3251 | 8.213 | 36.5959 | 34.0501 | 25.8844 | 24.6162 | 13.5613 | 8.419
800 | 20.4338 | 19.8367 | 800 | 18.0474 | 8.0008 | 34.6937 | 33.0881 | 20.4846 | 19.8861 | 11.9989 | 8.149
850 | 16.3013 | 15.946 | 850 | 14.7127 | 7.5793 | 10.1351 | 9.7229 | 16.3471 | 15.9908 | 10.6823 | 7.6961
900 | 11.3611 | 11.1537 | 900 | 9.9399 | 3.9782 | 7.4796 | 6.9518 | 11.3969 | 11.1888 | 6.4843 | 4.0242
950 | 7.7874 | 7.6911 | 950 | 6.8738 | 2.9618 | 3.7844 | 3.7021 | 7.8147 | 7.7181 | 4.5116 | 2.994
1000 | 4.8272 | 4.7896 | 1000 | 4.2477 | 1.7755 | 1.5447 | 1.5004 | 4.846 | 4.8083 | 2.715 | 1.7959
1050 | 2.5751 | 2.5705 | 1050 | 2.3216 | 1.2835 | 0.56291 | 0.55856 | 2.5862 | 2.5815 | 1.6334 | 1.2855
1100 | 1.831 | 1.8321 | 1100 | 1.7982 | 1.6575 | 0.34895 | 0.34531 | 1.8396 | 1.8407 | 1.6503 | 1.5874
1150 | 2.8432 | 2.8542 | 1150 | 2.573 | 1.5116 | 0.29702 | 0.28903 | 2.8578 | 2.8688 | 1.9171 | 1.5009
1200 | 4.6358 | 4.6696 | 1200 | 4.06 | 1.6719 | 0.27475 | 0.28528 | 4.6618 | 4.6958 | 2.4523 | 1.6536
1250 | 6.5658 | 6.6022 | 1250 | 5.9547 | 3.1155 | 0.18789 | 0.19582 | 6.6057 | 6.6424 | 4.1376 | 3.0573
1300 | 8.5169 | 8.5506 | 1300 | 7.9019 | 4.7465 | 0.24404 | 0.24118 | 8.573 | 8.6069 | 5.974 | 4.6244
1350 | 10.5572 | 10.583 | 1350 | 9.9193 | 6.4354 | 1.1171 | 1.0727 | 10.6322 | 10.6582 | 7.7561 | 6.2353
1400 | 12.4996 | 12.5407 | 1400 | 11.5589 | 7.0496 | 3.2745 | 3.1681 | 12.5951 | 12.6366 | 9.1298 | 6.7855
1450 | 14.2106 | 14.3539 | 1450 | 12.8832 | 6.7008 | 6.7111 | 6.7272 | 14.3272 | 14.4716 | 8.6343 | 6.421
1500 | 16.3502 | 16.4306 | 1500 | 15.2114 | 9.3129 | 4.5861 | 4.4501 | 16.4938 | 16.5749 | 11.309 | 8.8583
1550 | 18.9355 | 18.9577 | 1550 | 17.9305 | 11.9836 | 4.0711 | 3.8316 | 19.1132 | 19.1356 | 13.9262 | 11.3407
1600 | 20.9929 | 20.9751 | 1600 | 20.1033 | 14.0576 | 7.8206 | 7.3249 | 21.2029 | 21.1849 | 16.1448 | 13.274
1650 | 24.0389 | 23.7786 | 1650 | 23.58 | 18.7381 | 5.4485 | 5.0258 | 24.2948 | 24.0318 | 20.5567 | 17.5441
1700 | 26.0742 | 25.6687 | 1700 | 24.9799 | 17.8189 | 2.8754 | 2.3001 | 26.369 | 25.9589 | 22.9717 | 16.5493
1750 | 28.3083 | 28.891 | 1750 | 25.2729 | 11.78 | 2.5988 | 2.6751 | 28.6477 | 29.2374 | 15.9238 | 10.905
1800 | 32.9803 | 32.9676 | 1800 | 31.191 | 19.6836 | 4.0774 | 4.0805 | 33.3989 | 33.386 | 22.9974 | 18.0567
1850 | 37.1697 | 36.8148 | 1850 | 35.6423 | 24.2677 | 3.841 | 3.8822 | 37.6684 | 37.3087 | 28.1013 | 22.0851
1900 | 42.6702 | 42.064 | 1900 | 41.6282 | 30.9132 | 4.6291 | 4.5619 | 43.2744 | 42.6597 | 33.2548 | 27.8814
1950 | 50.6374 | 47.7625 | 1950 | 52.068 | 48.8628 | 4.2155 | 3.9795 | 51.3933 | 48.4755 | 49.4944 | 43.6678
2000 | 55.9759 | 54.2179 | 2000 | 55.4247 | 43.6077 | 3.6733 | 3.5999 | 56.8555 | 55.0698 | 46.2779 | 38.8137

## Cruiserath 220 kV
Terminal | Cruiserath 220 kV |  | Terminal | Cruiserath 220 kV
Terminal Name | Cruiserath 220 kV |  | Terminal Name | Cruiserath 220 kV_Clonee 220 kV |  | Cruiserath 220 kV_Corduff 110 kV |  | Cruiserath 220 kV_Corduff 220 kV |  | Cruiserath 220 kV_Woodland 220 kV
Study Case | step1 |  | Study Case | step1 |  | step1 |  | step1 |  | step1
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 8.2905 | 9.224 | 50 | 7.6244 | 5.7421 | 3.2039 | 3.4225 | 8.188 | 9.1214 | 6.2256 | 5.7842
100 | 20.9545 | 23.2998 | 100 | 19.5271 | 15.6572 | 8.4506 | 9.0211 | 20.7565 | 23.1011 | 16.5958 | 15.8441
150 | 38.6961 | 42.2877 | 150 | 37.4541 | 35.2157 | 17.8171 | 18.737 | 38.6161 | 42.1964 | 35.2199 | 35.7
200 | 10.0204 | 13.2714 | 200 | 8.972 | 10.7424 | 4.5323 | 4.6549 | 9.8839 | 13.051 | 9.254 | 10.8186
250 | 20.2026 | 26.8624 | 250 | 16.835 | 8.7874 | 5.6078 | 7.18 | 19.8294 | 26.4974 | 10.323 | 8.9926
300 | 70.1678 | 106.9943 | 300 | 62.4924 | 47.022 | 21.6946 | 32.1857 | 69.8204 | 106.7588 | 46.4387 | 48.9561
350 | 47.2561 | 44.2825 | 350 | 40.8423 | 15.4228 | 17.3284 | 15.7141 | 47.6498 | 44.8545 | 26.1712 | 15.9894
400 | 14.6366 | 13.489 | 400 | 13.0988 | 4.5822 | 6.3398 | 5.6191 | 15.3265 | 14.2003 | 7.6938 | 4.7311
450 | 5.9277 | 6.0371 | 450 | 4.6409 | 2.0709 | 2.462 | 2.4263 | 5.3181 | 5.4295 | 3.0155 | 2.1396
500 | 22.1858 | 23.8145 | 500 | 18.7959 | 9.877 | 11.6829 | 12.0228 | 21.2212 | 22.847 | 13.0264 | 10.1553
550 | 50.2434 | 59.6159 | 550 | 43.8088 | 26.6974 | 29.0624 | 32.2815 | 49.3241 | 58.6827 | 31.0833 | 27.3486
600 | 72.4714 | 99.7245 | 600 | 62.1672 | 36.7533 | 30.7548 | 41.7856 | 72.0163 | 99.4986 | 40.541 | 37.5782
650 | 90.2741 | 72.8058 | 650 | 77.4296 | 20.0435 | 49.4369 | 41.0557 | 90.9924 | 73.7655 | 43.7978 | 20.706
700 | 39.4077 | 35.7647 | 700 | 35.3812 | 12.897 | 30.6511 | 28.2217 | 40.6482 | 37.0356 | 22.2614 | 13.2221
750 | 24.6193 | 23.3126 | 750 | 22.3739 | 8.2309 | 36.6759 | 34.1245 | 25.8844 | 24.6162 | 13.591 | 8.4374
800 | 19.1295 | 18.5032 | 800 | 18.0923 | 8.0208 | 34.7801 | 33.1705 | 20.4846 | 19.8861 | 12.0287 | 8.1693
850 | 14.7435 | 14.3788 | 850 | 14.7541 | 7.6006 | 10.1636 | 9.7502 | 16.3471 | 15.9908 | 10.7124 | 7.7177
900 | 9.711 | 9.4882 | 900 | 9.9712 | 3.9907 | 7.5032 | 6.9737 | 11.3969 | 11.1888 | 6.5048 | 4.0369
950 | 6.0366 | 5.9333 | 950 | 6.8979 | 2.9722 | 3.7977 | 3.7151 | 7.8147 | 7.7181 | 4.5275 | 3.0045
1000 | 3.1124 | 3.0703 | 1000 | 4.2643 | 1.7824 | 1.5507 | 1.5063 | 4.846 | 4.8083 | 2.7256 | 1.8029
1050 | 1.7779 | 1.7704 | 1050 | 2.3316 | 1.289 | 0.56532 | 0.56095 | 2.5862 | 2.5815 | 1.6404 | 1.291
1100 | 3.1365 | 3.1389 | 1100 | 1.8067 | 1.6653 | 0.3506 | 0.34693 | 1.8396 | 1.8407 | 1.6581 | 1.5949
1150 | 4.9361 | 4.9487 | 1150 | 2.5863 | 1.5194 | 0.29855 | 0.29052 | 2.8578 | 2.8688 | 1.927 | 1.5086
1200 | 7.008 | 7.0417 | 1200 | 4.0828 | 1.6813 | 0.27629 | 0.28688 | 4.6618 | 4.6958 | 2.4661 | 1.6629
1250 | 9.1076 | 9.1445 | 1250 | 5.9909 | 3.1345 | 0.18903 | 0.19701 | 6.6057 | 6.6424 | 4.1628 | 3.076
1300 | 11.2073 | 11.2427 | 1300 | 7.9539 | 4.7777 | 0.24565 | 0.24277 | 8.573 | 8.6069 | 6.0133 | 4.6548
1350 | 13.3954 | 13.4229 | 1350 | 9.9898 | 6.4812 | 1.125 | 1.0803 | 10.6322 | 10.6582 | 7.8112 | 6.2796
1400 | 15.4719 | 15.5216 | 1400 | 11.6473 | 7.1035 | 3.2995 | 3.1923 | 12.5951 | 12.6366 | 9.1996 | 6.8374
1450 | 17.3341 | 17.4819 | 1450 | 12.9889 | 6.7558 | 6.7661 | 6.7824 | 14.3272 | 14.4716 | 8.7051 | 6.4737
1500 | 19.6343 | 19.7201 | 1500 | 15.345 | 9.3947 | 4.6263 | 4.4892 | 16.4938 | 16.5749 | 11.4083 | 8.9361
1550 | 22.3905 | 22.4164 | 1550 | 18.0988 | 12.096 | 4.1093 | 3.8675 | 19.1132 | 19.1356 | 14.0569 | 11.4472
1600 | 24.6136 | 24.5994 | 1600 | 20.3044 | 14.1982 | 7.8988 | 7.3982 | 21.2029 | 21.1849 | 16.3063 | 13.4067
1650 | 27.8492 | 27.59 | 1650 | 23.831 | 18.9376 | 5.5065 | 5.0793 | 24.2948 | 24.0318 | 20.7755 | 17.7308
1700 | 30.0276 | 29.6481 | 1700 | 25.2623 | 18.0204 | 2.9079 | 2.3261 | 26.369 | 25.9589 | 23.2315 | 16.7364
1750 | 32.4903 | 33.1006 | 1750 | 25.5759 | 11.9212 | 2.63 | 2.7072 | 28.6477 | 29.2374 | 16.1147 | 11.0357
1800 | 37.4311 | 37.4249 | 1800 | 31.5869 | 19.9334 | 4.1292 | 4.1323 | 33.3989 | 33.386 | 23.2893 | 18.2859
1850 | 41.8618 | 41.5147 | 1850 | 36.1205 | 24.5933 | 3.8925 | 3.9342 | 37.6684 | 37.3087 | 28.4783 | 22.3814
1900 | 47.6886 | 47.0748 | 1900 | 42.2177 | 31.351 | 4.6946 | 4.6265 | 43.2744 | 42.6597 | 33.7257 | 28.2762
1950 | 55.9971 | 53.0619 | 1950 | 52.8452 | 49.5921 | 4.2784 | 4.0389 | 51.3933 | 48.4755 | 50.2332 | 44.3196
2000 | 61.7068 | 59.9198 | 2000 | 56.2956 | 44.2929 | 3.731 | 3.6564 | 56.8555 | 55.0698 | 47.0051 | 39.4236

## Woodland 220 kV
Terminal | Woodland 220 kV |  | Terminal | Woodland 220 kV
Terminal Name | Woodland 220 kV |  | Terminal Name | Woodland 220 kV_Clonee 220 kV |  | Woodland 220 kV_Corduff 110 kV |  | Woodland 220 kV_Corduff 220 kV |  | Woodland 220 kV_Cruiserath 220 kV
Study Case | step1 |  | Study Case | step1 |  | step1 |  | step1 |  | step1
Contingency | Base_Case | CLO2-CDU2-ckt1 | Contingency | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1 | Base_Case | CLO2-CDU2-ckt1
Filter Details |  |  | Filter Details
Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | Full Result Name | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1 | step1_Base_Case | step1_CLO2-CDU2-ckt1
Result Type | m:Z | m:Z | Result Type | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12 | c:Z_12
Frequency in Hz |  |  | Frequency in Hz
50 | 7.3598 | 7.6181 | 50 | 6.5241 | 7.5443 | 2.6391 | 2.4797 | 6.2256 | 5.7842 | 6.2256 | 5.7842
100 | 18.5002 | 18.8528 | 100 | 17.0574 | 18.5897 | 7.2264 | 6.913 | 16.5952 | 15.8434 | 16.5958 | 15.8441
150 | 33.9486 | 33.0488 | 150 | 34.6762 | 32.5685 | 16.6621 | 16.5193 | 35.2168 | 35.6968 | 35.2199 | 35.7
200 | 7.1395 | 6.9384 | 200 | 8.3287 | 6.7536 | 5.3575 | 5.7616 | 9.2526 | 10.8169 | 9.254 | 10.8186
250 | 13.2886 | 14.2748 | 250 | 10.6326 | 13.6816 | 3.7729 | 3.6933 | 10.3205 | 8.9904 | 10.323 | 8.9926
300 | 39.6187 | 32.8441 | 300 | 43.9273 | 31.5845 | 15.0595 | 15.7653 | 46.4223 | 48.9389 | 46.4387 | 48.9561
350 | 7.9318 | 13.7894 | 350 | 20.0712 | 13.3517 | 9.2889 | 5.1578 | 26.1587 | 15.9818 | 26.1712 | 15.9894
400 | 11.8163 | 18.5794 | 400 | 3.4144 | 18.0235 | 2.8618 | 1.6532 | 7.689 | 4.7282 | 7.6938 | 4.7311
450 | 20.2219 | 26.7337 | 450 | 7.2033 | 25.9175 | 2.6646 | 2.7121 | 3.0131 | 2.1379 | 3.0155 | 2.1396
500 | 29.8675 | 35.5401 | 500 | 17.4132 | 34.5275 | 9.2829 | 8.3889 | 13.0137 | 10.1454 | 13.0264 | 10.1553
550 | 39.1304 | 41.171 | 550 | 32.723 | 40.1467 | 21.9899 | 20.2261 | 31.0468 | 27.3164 | 31.0833 | 27.3486
600 | 30.4974 | 27.4332 | 600 | 36.2712 | 26.7232 | 23.7436 | 24.867 | 40.4843 | 37.5256 | 40.541 | 37.5782
650 | 19.3739 | 32.2385 | 650 | 32.6965 | 31.5614 | 27.7139 | 17.0245 | 43.7259 | 20.672 | 43.7978 | 20.706
700 | 20.4988 | 39.3458 | 700 | 12.2156 | 38.675 | 19.7141 | 14.4684 | 22.219 | 13.197 | 22.2614 | 13.2221
750 | 24.7077 | 39.4083 | 750 | 5.9959 | 38.6051 | 19.7467 | 12.5029 | 13.5613 | 8.419 | 13.591 | 8.4374
800 | 29.5043 | 47.0385 | 800 | 5.1347 | 46.2518 | 22.8063 | 17.0607 | 11.9989 | 8.149 | 12.0287 | 8.1693
850 | 34.6218 | 57.1044 | 850 | 3.1559 | 56.3985 | 6.9386 | 5.164 | 10.6823 | 7.6961 | 10.7124 | 7.7177
900 | 38.9247 | 58.934 | 900 | 6.4973 | 58.4914 | 6.4517 | 9.0156 | 6.4843 | 4.0242 | 6.5048 | 4.0369
950 | 40.3138 | 59.4043 | 950 | 8.3235 | 59.2481 | 3.682 | 3.5352 | 4.5116 | 2.994 | 4.5275 | 3.0045
1000 | 43.4447 | 62.5554 | 1000 | 10.6186 | 62.669 | 1.4888 | 1.6826 | 2.715 | 1.7959 | 2.7256 | 1.8029
1050 | 42.3028 | 57.2824 | 1050 | 11.3092 | 57.4301 | 1.9613 | 2.4557 | 1.6334 | 1.2855 | 1.6404 | 1.291
1100 | 47.8643 | 67.1156 | 1100 | 13.6994 | 67.5092 | 1.4754 | 2.047 | 1.6503 | 1.5874 | 1.6581 | 1.5949
1150 | 50.7375 | 69.4277 | 1150 | 15.4014 | 70.0137 | 0.5562 | 0.64144 | 1.9171 | 1.5009 | 1.927 | 1.5086
1200 | 48.9562 | 66.0395 | 1200 | 15.527 | 66.986 | 1.1156 | 1.5716 | 2.4523 | 1.6536 | 2.4661 | 1.6629
1250 | 59.8492 | 85.167 | 1250 | 19.9365 | 86.9079 | 0.51905 | 0.83748 | 4.1376 | 3.0573 | 4.1628 | 3.076
1300 | 69.9708 | 103.3484 | 1300 | 24.2587 | 106.1212 | 1.1679 | 1.7724 | 5.974 | 4.6244 | 6.0133 | 4.6548
1350 | 75.734 | 113.3798 | 1350 | 27.2763 | 117.0184 | 2.1039 | 2.6699 | 7.7561 | 6.2353 | 7.8112 | 6.2796
1400 | 77.6215 | 106.8885 | 1400 | 28.9276 | 111.0499 | 3.7632 | 3.6974 | 9.1298 | 6.7855 | 9.1996 | 6.8374
1450 | 66.2301 | 89.5351 | 1450 | 25.3451 | 93.3798 | 2.2132 | 2.313 | 8.6343 | 6.421 | 8.7051 | 6.4737
1500 | 78.958 | 111.5666 | 1500 | 31.0376 | 117.0218 | 7.4673 | 9.6831 | 11.309 | 8.8583 | 11.4083 | 8.9361
1550 | 89.1499 | 131.5292 | 1550 | 35.9775 | 138.7185 | 7.9392 | 10.3461 | 13.9262 | 11.3407 | 14.0569 | 11.4472
1600 | 100.5841 | 155.3346 | 1600 | 41.0502 | 164.9185 | 15.0147 | 20.0832 | 16.1448 | 13.274 | 16.3063 | 13.4067
1650 | 115.519 | 180.5017 | 1650 | 48.8478 | 192.9807 | 9.4383 | 12.2668 | 20.5567 | 17.5441 | 20.7755 | 17.7308
1700 | 118.4173 | 154.6882 | 1700 | 51.6532 | 166.5576 | 9.7836 | 12.1592 | 22.9717 | 16.5493 | 23.2315 | 16.7364
1750 | 76.935 | 96.1594 | 1750 | 34.3509 | 103.9499 | 0.88885 | 0.83531 | 15.9238 | 10.905 | 16.1147 | 11.0357
1800 | 101.9305 | 143.2389 | 1800 | 47.1397 | 156.2721 | 1.241 | 0.50492 | 22.9974 | 18.0567 | 23.2893 | 18.2859
1850 | 114.2866 | 158.4383 | 1850 | 54.7841 | 174.2118 | 1.7282 | 2.7178 | 28.1013 | 22.0851 | 28.4783 | 22.3814
1900 | 124.9482 | 183.5857 | 1900 | 62.0172 | 203.6243 | 2.4883 | 1.8158 | 33.2548 | 27.8814 | 33.7257 | 28.2762
1950 | 170.9294 | 262.7378 | 1950 | 88.2134 | 294.0785 | 3.1573 | 1.8658 | 49.4944 | 43.6678 | 50.2332 | 44.3196
2000 | 144.5227 | 206.5382 | 2000 | 77.9919 | 232.1325 | 2.2843 | 1.8859 | 46.2779 | 38.8137 | 47.0051 | 39.4236